## Stateline 138 kV
Stateline 138 kV
Model | Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
AG1 LL 2024 LL NonDiv NonMTX | STILLWELL - DUMONT Ckt #1 345 kV | 345 | 1409 | Single | COMED_P1-2_765-L11215__-S | 146.13 | 149.35 | 0.19638 | 43.2044 | 100 | 36.64 | 6.7555 | 36.64 | - | 36.64
AG1 LL 2024 LL NonDiv NonMTX | GREENACRE_T - OLIVE Ckt #1 345 kV | 345 | 971 | Single | AEP_P1-2_#695_1681 | 116.99 | 122.64 | 0.09265 | 20.3832 | 100 | 27.8008 | 27.8008 | 150.784 | - | 27.8008
AG1 LL 2024 LL NonDiv NonMTX | GREEN_ACRE - GREENACRE_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 104.13 | 109.15 | 0.09265 | 20.3832 | 100 | 0.0944 | 0.0944 | 0.512 | - | 0.0944
AG1 LL 2024 LL NonDiv NonMTX | DUMONT - SORENS Ckt #1 765 kV | 765 | 4142 | Breaker | AEP_P4_#7334_05JEFRSO 765_A2 | 100.22 | 102.01 | 0.22935 | 50.457 | 100 | 7.63 | 7.63 | 7.63 | - | 7.63
AG1 SIS 2024 TARA NonDiv NonMTX | JEFRSO - CLIFTY Ckt #Z1 345 kV | 345 | 1868 | Single | AEP_P1-2_#709_546 | 175.93 | 178.24 | 0.10433 | 22.953 | 100 | 2.56 | 0.472 | 2.56 | - | 2.56
AG1 SIS 2024 TARA NonDiv NonMTX | AF2-359_TAP - OLIVE Ckt #1 345 kV | 345 | 971 | Single | COMED_P1-2_765-L11215__-S | 174.35 | 177.3 | 0.08038 | 17.6834 | 100 | 23.456 | 4.3247 | 23.456 | - | 23.456
AG1 SIS 2024 TARA NonDiv NonMTX | UNIV_PK_N_RP - AF2-359_TAP Ckt #1 345 kV | 345 | 971 | Single | COMED_P1-2_765-L11215__-S | 152.74 | 155.13 | 0.08038 | 17.6834 | 100 | 210.944 | 38.8928 | 210.944 | - | 210.944
AG1 SIS 2024 TARA NonDiv NonMTX | ST_JOHN_T - GREEN_ACRE Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 128.27 | 130.76 | 0.06613 | 14.5484 | 100 | 0.0944 | 0.0944 | 0.512 | - | 0.0944
AG1 SIS 2024 TARA NonDiv NonMTX | STJOHN - ST_JOHN_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 128.27 | 130.75 | 0.06613 | 14.5484 | 100 | 4.0002 | 4.0002 | 21.696 | - | 4.0002

## Calumet 138 kV
Calumet 138 kV
Model | Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
AG1 LL 2024 LL | STILLWELL - DUMONT Ckt #1 345 kV | 345 | 1409 | Single | COMED_P1-2_765-L11215__-S | 146.12 | 149.34 | 0.19578 | 43.0726 | 100 | 36.64 | 6.7555 | 36.64 | - | 36.64
AG1 LL 2024 LL | GREENACRE_T - OLIVE Ckt #1 345 kV | 345 | 971 | Single | AEP_P1-2_#695_1681 | 116.99 | 122.64 | 0.09257 | 20.366 | 100 | 27.8008 | 27.8008 | 150.784 | - | 27.8008
AG1 LL 2024 LL | GREEN_ACRE - GREENACRE_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 104.13 | 109.15 | 0.09257 | 20.366 | 100 | 0.0944 | 0.0944 | 0.512 | - | 0.0944
AG1 LL 2024 LL | DUMONT - SORENS Ckt #1 765 kV | 765 | 4142 | Breaker | AEP_P4_#7334_05JEFRSO 765_A2 | 100.22 | 102.01 | 0.2294 | 50.4684 | 100 | 7.63 | 7.63 | 7.63 | - | 7.63
AG1 SIS 2024 TARA | JEFRSO - CLIFTY Ckt #Z1 345 kV | 345 | 1868 | Single | AEP_P1-2_#709_546 | 175.93 | 178.24 | 0.10432 | 22.9505 | 100 | 2.56 | 0.472 | 2.56 | - | 2.56
AG1 SIS 2024 TARA | AF2-359_TAP - OLIVE Ckt #1 345 kV | 345 | 971 | Single | COMED_P1-2_765-L11215__-S | 174.36 | 177.31 | 0.0809 | 17.7971 | 100 | 23.456 | 4.3247 | 23.456 | - | 23.456
AG1 SIS 2024 TARA | CRETE_EC_BP - STJOHN Ckt #1 345 kV | 345 | 1399 | Single | AEP_P1-2_#695_1681 | 154.14 | 157.5 | 0.06309 | 9.0675 | 100 | 38.368 | 7.0741 | 38.368 | - | 38.368
AG1 SIS 2024 TARA | UNIV_PK_N_RP - AF2-359_TAP Ckt #1 345 kV | 345 | 971 | Single | COMED_P1-2_765-L11215__-S | 152.75 | 155.14 | 0.0809 | 17.7971 | 100 | 210.944 | 38.8928 | 210.944 | - | 210.944
AG1 SIS 2024 TARA | ST_JOHN_T - GREEN_ACRE Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 128.28 | 130.76 | 0.06673 | 14.6801 | 100 | 0.0944 | 0.0944 | 0.512 | - | 0.0944
AG1 SIS 2024 TARA | STJOHN - ST_JOHN_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 128.29 | 130.76 | 0.06673 | 14.6801 | 100 | 4.0002 | 4.0002 | 21.696 | - | 4.0002
AG1 SIS 2024 TARA | JEFRSO - JEFRSO Ckt #2 765/345 kV | 765/345 | 3039 | Single | AEP_P1-2_#709_546 | 108.14 | 110.45 | 0.10432 | 22.9505 | 100 | 18 | - | - | 18 | 18

## Stateline 345 kV
Stateline 345 kV
Model | Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
AG1 LL 2024 LL | STILLWELL - DUMONT Ckt #1 345 kV | 345 | 1409 | Single | COMED_P1-2_765-L11215__-S | 146.22 | 149.48 | 0.2001 | 44.0211 | 100 | 36.64 | 6.7555 | 36.64 | - | 36.64
AG1 LL 2024 LL | GREENACRE_T - OLIVE Ckt #1 345 kV | 345 | 971 | Single | AEP_P1-2_#695_1681 | 116.97 | 122.47 | 0.09128 | 20.0826 | 100 | 27.8008 | 27.8008 | 150.784 | - | 27.8008
AG1 LL 2024 LL | GREEN_ACRE - GREENACRE_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 104.11 | 109 | 0.09128 | 20.0826 | 100 | 0.0944 | 0.0944 | 0.512 | - | 0.0944
AG1 LL 2024 LL | DUMONT - SORENS Ckt #1 765 kV | 765 | 4142 | Breaker | AEP_P4_#7334_05JEFRSO 765_A2 | 100.23 | 101.94 | 0.22967 | 50.527 | 100 | 7.63 | 7.63 | 7.63 | - | 7.63
AG1 SIS 2024 TARA | JEFRSO - CLIFTY Ckt #Z1 345 kV | 345 | 1868 | Single | AEP_P1-2_#709_546 | 175.93 | 178.24 | 0.10432 | 22.9494 | 100 | 2.56 | 0.472 | 2.56 | - | 2.56
AG1 SIS 2024 TARA | AF2-359_TAP - OLIVE Ckt #1 345 kV | 345 | 971 | Single | COMED_P1-2_765-L11215__-S | 174.37 | 177.31 | 0.08103 | 17.8266 | 100 | 23.456 | 4.3247 | 23.456 | - | 23.456
AG1 SIS 2024 TARA | CRETE_EC_BP - STJOHN Ckt #1 345 kV | 345 | 1399 | Single | AEP_P1-2_#695_1681 | 154.21 | 157.55 | 0.06733 | 14.8122 | 100 | 38.368 | 7.0741 | 38.368 | - | 38.368
AG1 SIS 2024 TARA | UNIV_PK_N_RP - AF2-359_TAP Ckt #1 345 kV | 345 | 971 | Single | COMED_P1-2_765-L11215__-S | 152.76 | 155.14 | 0.08103 | 17.8266 | 100 | 210.944 | 38.8928 | 210.944 | - | 210.944
AG1 SIS 2024 TARA | ST_JOHN_T - GREEN_ACRE Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 128.32 | 130.79 | 0.06821 | 15.0053 | 100 | 0.0944 | 0.0944 | 0.512 | - | 0.0944
AG1 SIS 2024 TARA | STJOHN - ST_JOHN_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 128.32 | 130.78 | 0.06821 | 15.0053 | 100 | 4.0002 | 4.0002 | 21.696 | - | 4.0002
AG1 SIS 2024 TARA | HAYES - BEAVER Ckt #1 345 kV | 345 | 1844 | Single | BEAVER -AD1-103 TAP 345 kV ckt 1 | 118.74 | 119.28 | 0.05894 | 12.9657 | 100 | 35.105 | 35.105 | 190.4 | - | 35.105
AG1 SIS 2024 TARA | SORENS - AF2-137_TAP Ckt #1 765 kV | 765 | 4142 | Single | AEP_P1-2_#709_546 | 116.48 | 117.55 | 0.24096 | 53.0103 | 100 | 45.78 | 45.78 | 45.78 | - | 45.78
AG1 SIS 2024 TARA | JEFRSO - JEFRSO Ckt #2 765/345 kV | 765/345 | 3039 | Single | AEP_P1-2_#709_546 | 108.14 | 110.45 | 0.10432 | 22.9494 | 100 | 18 | - | - | 18 | 18

## Calumet 345 kV
Calumet 345 kV
Model | Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
AG1 LL 2024 LL | STILLWELL - DUMONT Ckt #1 345 kV | 345 | 1409 | Single | COMED_P1-2_765-L11215__-S | 145.92 | 149.17 | 0.18111 | 39.845 | 100 | 36.64 | 6.7555 | 36.64 | - | 36.64
AG1 LL 2024 LL | GREENACRE_T - OLIVE Ckt #1 345 kV | 345 | 971 | Single | AEP_P1-2_#695_1681 | 116.96 | 122.48 | 0.09078 | 19.9715 | 100 | 27.8008 | 27.8008 | 150.784 | - | 27.8008
AG1 LL 2024 LL | GREEN_ACRE - GREENACRE_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 104.1 | 109.01 | 0.09078 | 19.9715 | 100 | 0.0944 | 0.0944 | 0.512 | - | 0.0944
AG1 LL 2024 LL | WILTON_4M - WILTON Ckt #1 345/765 kV | 345/765 | 1379 | Single | COMED_P1-2_765-L11216__-S | 101.22 | 103.18 | 0.09973 | 21.9414 | 100 | 18 | - | - | 18 | 18
AG1 LL 2024 LL | DUMONT - SORENS Ckt #1 765 kV | 765 | 4142 | Breaker | AEP_P4_#7334_05JEFRSO 765_A2 | 100.24 | 102.03 | 0.23043 | 50.6953 | 100 | 7.63 | 7.63 | 7.63 | - | 7.63
AG1 SIS 2024 TARA | JEFRSO - CLIFTY Ckt #Z1 345 kV | 345 | 1868 | Single | AEP_P1-2_#709_546 | 175.93 | 178.23 | 0.10396 | 22.8721 | 100 | 2.56 | 0.472 | 2.56 | - | 2.56
AG1 SIS 2024 TARA | AF2-359_TAP - OLIVE Ckt #1 345 kV | 345 | 971 | Single | COMED_P1-2_765-L11215__-S | 174.65 | 177.59 | 0.09336 | 20.5394 | 100 | 23.456 | 4.3247 | 23.456 | - | 23.456
AG1 SIS 2024 TARA | CRETE_EC_BP - STJOHN Ckt #1 345 kV | 345 | 1399 | Single | AEP_P1-2_#695_1681 | 154.7 | 158.04 | 0.09882 | 21.7399 | 100 | 38.368 | 7.0741 | 38.368 | - | 38.368
AG1 SIS 2024 TARA | UNIV_PK_N_RP - AF2-359_TAP Ckt #1 345 kV | 345 | 971 | Single | COMED_P1-2_765-L11215__-S | 153.03 | 155.42 | 0.09336 | 20.5394 | 100 | 210.944 | 38.8928 | 210.944 | - | 210.944
AG1 SIS 2024 TARA | ST_JOHN_T - GREEN_ACRE Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 128.61 | 131.07 | 0.08255 | 18.1611 | 100 | 0.0944 | 0.0944 | 0.512 | - | 0.0944
AG1 SIS 2024 TARA | STJOHN - ST_JOHN_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 128.61 | 131.07 | 0.08255 | 18.1611 | 100 | 4.0002 | 4.0002 | 21.696 | - | 4.0002
AG1 SIS 2024 TARA | JEFRSO - JEFRSO Ckt #2 765/345 kV | 765/345 | 3039 | Single | AEP_P1-2_#709_546 | 108.14 | 110.45 | 0.10396 | 22.8721 | 100 | 18 | - | - | 18 | 18
AG1 SIS 2024 TARA | BURNHAM_B - SHEFFIELD Ckt #1 345 kV | 345 | 1441 | Single | COMED_P1-2_765-L11215__-S | 104.11 | 106.13 | 0.26088 | 57.3941 | 100 | 3.3158 | 3.3158 | 17.984 | - | 3.3158

## North Harbor 138 kV
N Harbor 138 kV
Model | Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
AG1 LL 2024 LL | STILLWELL - DUMONT Ckt #1 345 kV | 345 | 1409 | Single | COMED_P1-2_765-L11215__-S | 146.12 | 149.35 | 0.19591 | 43.1 | 100 | 36.64 | 6.7555 | 36.64 | - | 36.64
AG1 LL 2024 LL | GREENACRE_T - OLIVE Ckt #1 345 kV | 345 | 971 | Single | AEP_P1-2_#695_1681 | 116.99 | 122.64 | 0.09259 | 20.3696 | 100 | 27.8008 | 27.8008 | 150.784 | - | 27.8008
AG1 LL 2024 LL | GREEN_ACRE - GREENACRE_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 104.13 | 109.15 | 0.09259 | 20.3696 | 100 | 0.0944 | 0.0944 | 0.512 | - | 0.0944
AG1 LL 2024 LL | DUMONT - SORENS Ckt #1 765 kV | 765 | 4142 | Breaker | AEP_P4_#7334_05JEFRSO 765_A2 | 100.22 | 102.01 | 0.22939 | 50.466 | 100 | 7.63 | 7.63 | 7.63 | - | 7.63
AG1 SIS 2024 TARA | JEFRSO - CLIFTY Ckt #Z1 345 kV | 345 | 1868 | Single | AEP_P1-2_#709_546 | 175.93 | 178.24 | 0.10432 | 22.951 | 100 | 2.56 | 0.472 | 2.56 | - | 2.56
AG1 SIS 2024 TARA | AF2-359_TAP - OLIVE Ckt #1 345 kV | 345 | 971 | Single | COMED_P1-2_765-L11215__-S | 174.35 | 177.31 | 0.08079 | 17.7734 | 100 | 23.456 | 4.3247 | 23.456 | - | 23.456
AG1 SIS 2024 TARA | CRETE_EC_BP - STJOHN Ckt #1 345 kV | 345 | 1399 | Single | AEP_P1-2_#695_1681 | 154.14 | 157.5 | 0.0628 | 9.0399 | 100 | 38.368 | 7.0741 | 38.368 | - | 38.368
AG1 SIS 2024 TARA | UNIV_PK_N_RP - AF2-359_TAP Ckt #1 345 kV | 345 | 971 | Single | COMED_P1-2_765-L11215__-S | 152.74 | 155.13 | 0.08079 | 17.7734 | 100 | 210.944 | 38.8928 | 210.944 | - | 210.944
AG1 SIS 2024 TARA | ST_JOHN_T - GREEN_ACRE Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 128.28 | 130.76 | 0.0666 | 14.6527 | 100 | 0.0944 | 0.0944 | 0.512 | - | 0.0944
AG1 SIS 2024 TARA | STJOHN - ST_JOHN_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 128.28 | 130.76 | 0.0666 | 14.6527 | 100 | 4.0002 | 4.0002 | 21.696 | - | 4.0002
AG1 SIS 2024 TARA | JEFRSO - JEFRSO Ckt #2 765/345 kV | 765/345 | 3039 | Single | AEP_P1-2_#709_546 | 108.14 | 110.45 | 0.10432 | 22.951 | 100 | 18 | N/A | N/A | 18 | 18