## J1882
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | LOCKPORT - KENDALL 345 kV ckt 1 | 345 | 16.06 | 222 | CE | Base Case | 116.44 | 114.11 | 79.48 | 0.05759 | 2.62 | 3.3% | 0.31 | 9.4754 | 51.392 | - | 9.4754
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement (Transformer) Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | LOCKPORT - KENDALL 345 kV ckt 1 | 16.06 | - | 345 | 1448 | 222 | CE | Base Case | 127.49 | 1687.14 | 158.9 | 5.78% | 2.6 | 117.63 | 9.4754 | 51.392 | - | 2.21% | ER Upgrade
NRIS | MASON_IL 138/69.0 kV xfmr 1 | - | - | 138/69 | 56 | 357 | AMIL | Base Case | 123.74 | 36.72 | 32.57 | 6.69% | 3.01 | 3.01 | - | - | 6 | 100% | 6

## J1973
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | CAYUGA - 08NUCOR 345 kV ckt 1 | 32.29 | - | 345 | 1279 | 208 | DEI | OLIVE - AF1-215 TAP 345 kV ckt 2 | 114.16 | 1066.61 | 393.53 | 7.48% | 2.99 | 203.77 | 19.0511 | 103.328 | 1.47% | 0.2795
NRIS | ROCKPT - JEFRSO 765 kV ckt 1 | 128.91 | - | 765 | 3854 | 205 | AEP | J2201 POI - KENZIG ROAD 345 kV ckt 1 | 106.81 | 3332.82 | 593.6 | 7.35% | 2.94 | 329 | 140.5119 | - | 0.89% | 1.2556
NRIS | NUCOR - WHITST 345 kV ckt 1 | 27.99 | - | 345 | 1195 | 208 | DEI | OLIVE - AF1-215 TAP 345 kV ckt 2 | 101.02 | 811.21 | 393.53 | 7.48% | 2.99 | 203.77 | 16.5141 | 89.568 | 1.47% | 0.2423

## J1975
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | ROCKPT - JEFRSO 765 kV ckt 1 | 128.91 | - | 765 | 3854 | 205 | AEP | J2201 POI - KENZIG ROAD 345 kV ckt 1 | 106.81 | 3332.82 | 593.6 | 10.07% | 4.03 | 329 | 140.5119 | - | 1.22% | 1.721

## J2124
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Sh Charging | MAHOMET_2 - MAHOMET_1 Ckt #Z 138 kV | 138 | 0.1 | 357 | AMIL | P23:345:AMIL::RISING:V13 | 105.63 | 84.59 | 21.11 | -0.21315 | 21.11 | 100% | 0.04 | 0.037 | 0.17 | - | 0.037
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | CAYUGA - NUCOR Ckt #1 345 kV | 32.29 | - | 345 | 1279 | 208 | DEI | OLIVE - AF1-215 TAP 345 kV ckt 2 | 114.16 | 1066.61 | 393.53 | 6.66% | 6.66 | 203.77 | 19.0511 | 103.328 | 3.27% | 0.6227
NRIS | ROCKPT - JEFRSO Ckt #1 765 kV | 128.91 | - | 765 | 3854 | 205 | AEP | J2201 POI - KENZIG ROAD 345 kV ckt 1 | 106.81 | 3332.82 | 593.6 | 6.59% | 6.59 | 329 | 140.5119 | - | 2% | 2.8145
NRIS | NUCOR - WHITST Ckt #1 345 kV | 27.99 | - | 345 | 1195 | 208 | DEI | OLIVE - AF1-215 TAP 345 kV ckt 2 | 101.02 | 811.21 | 393.53 | 6.66% | 6.66 | 203.77 | 16.5141 | 89.568 | 3.27% | 0.5397

## J2159
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | HUTSONVL - HEATH Ckt #1 138 kV | 11.4 | - | 138 | 175 | 357 | AMIL | Base Case | 118.61 | 83.08 | 124.48 | 29.58% | 29.58 | 44.37 | 4.218 | 19.38 | 66.67% | 2.812
NRIS | ROCKPT - JEFRSO Ckt #1 765 kV | 128.91 | - | 765 | 3854 | 205 | AEP | J2201 POI - KENZIG ROAD 345 kV ckt 1 | 106.81 | 3332.82 | 593.6 | 10.25% | 10.25 | 329 | 140.5119 | - | 3.12% | 4.378

## J2161
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | LOCKPORT_B - KENDALL _BU Ckt #1 345 kV | 345 | 16.06 | 222 | CE | Base Case | 116.44 | 114.11 | 79.48 | 0.05659 | 2.85 | 3.59% | 0.34 | 9.4754 | 51.392 | - | 9.4754
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | KENDALL_BU - LOCKPORT_B Ckt #1 345 kV | 16.06 | - | 345 | 1448 | 222 | CE | Base Case | 127.49 | 1687.14 | 158.9 | 5.68% | 5.68 | 117.63 | 9.4754 | 51.392 | 4.83% | ER Upgrade
NRIS | J2186_POI - 7MAPLE_RIDGE Ckt #1 345 kV | 23.21 | - | 345 | 1195 | 357 | AMIL | AA2-116_POI - AA2-116_MAIN 345 kV ckt 1 | 117.22 | 369.12 | 1031.68 | 30.37% | 30.4 | 714.23 | 13.6939 | 74.272 | 4.26% | 0.5829

## J2170
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | JEFRSO - ROCKPT Ckt #1 765 kV | 765 | 110 | 205 | AEP | P7:345:AEP:I&M SULLIVAN - AEP DARWIN 345 | 101.05 | 104.7 | 47.58 | 0.31499 | 47.58 | 100% | 119.9 | 119.9 | 119.9 | - | 119.9
Sh Charging | J1701_POI - IPAVA_1 Ckt #1 138kV | 138 | 7.6 | 901/357 | Are_901/AMIL | Base Case | 108.08 | 112.7 | 4.82 | -0.09709 | 4.82 | 100% | 2.81 | 2.812 | 12.92 | - | 2.812
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | ROCKPT - JEFRSO Ckt #1 765 kV | 128.91 | - | 765 | 3854 | 205 | AEP | 52016 J2201 POI 345 326569 7KENZIG ROAD 345 1 | 106.81 | 3332.82 | 593.6 | 24.01% | 36.02 | 329 | 140.5119 | - | 10.95% | ER Upgrade

## J2195
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Sh Charging | J1145_POI - J1965_POI Ckt #1 345 kV | 345 | 9.46 | 356 | AMMO | Base Case | 180.18 | 162.97 | 118.71 | -0.05141 | 5.21 | 4.39% | 1.33 | 5.5814 | 30.272 | - | 30.272
Sh Charging | J1965_POI - MONTGMRY Ckt #1 345 kV | 345 | 18.54 | 356 | AMMO | Base Case | 173.69 | 162.86 | 97.15 | -0.05144 | 5.22 | 5.37% | 3.19 | 10.9386 | 59.328 | - | 59.328
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | AE1-172_TAP - AD1-100_TAP2 Ckt #1 345 kV | 14.69 | - | 345 | 1364 | 222 | CE | Base Case | 114.48 | 802.4 | 759.12 | 6.68% | 6.68 | 174.05 | 8.6671 | 47.008 | 3.84% | 0.3326
NRIS | ROCKPT - JEFRSO Ckt #1 765 kV | 128.91 | - | 765 | 3854 | 205 | AEP | J2201 POI 345 - 7KENZIG ROAD 345 1 | 106.81 | 3332.82 | 593.6 | 8.16% | 8.16 | 329 | 140.5119 | - | 2.48% | 3.485

## J2197
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Sh Charging | J1145_POI - J1965_POI Ckt #1 345 kV | 345 | 9.46 | 356 | AMMO | Base Case | 180.18 | 162.97 | 118.71 | -0.05216 | 5.29 | 4.46% | 1.35 | 5.5814 | 30.272 | - | 30.272
Sh Charging | J1965_POI - MONTGMRY Ckt #1 345 kV | 345 | 18.54 | 356 | AMMO | Base Case | 173.69 | 162.86 | 97.15 | -0.05219 | 5.29 | 5.45% | 3.23 | 10.9386 | 59.328 | - | 59.328
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | ROCKPT - JEFRSO Ckt #1 765 kV | 128.91 | - | 765 | 3854 | 205 | AEP | J2201 POI 345 - 7KENZIG ROAD 345 1 | 106.81 | 3332.82 | 593.6 | 9.03% | 9.03 | 329 | 140.5119 | - | 2.74% | 3.8566

## J2376
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | SIOUX - ROXFORD Ckt #1 345 kV | 345 | 12.7 | 356/357 | AMMO/AMIL | Base Case | 147.4 | 24.79 | 837.77 | 0.05076 | 5.08 | 0.61% | 0.25 | 7.493 | 40.64 | 40.64
Summer Peak | JEFRSO - ROCKPT Ckt #1 765 kV | 765 | 110 | 205 | AEP | Base Case | 113.92 | 111.18 | 479.1 | 0.06677 | 6.68 | 1.39% | 1.67 | 119.9 | 119.9 | 119.9
Summer Peak | ORETTO_B - AD1-100_TAP Ckt #1 345 kV | 345 | 20 | 222 | CE | Base Case | 104.42 | 62.25 | 407.06 | 0.06623 | 6.62 | 1.63% | 0.19 | 11.8 | 64 | 11.8
Summer Peak | ORETTO_B - PONTIAC_B Ckt #1 345 kV | 345 | 11.47 | 222 | CE | Base Case | 102.11 | 59.9 | 407.06 | 0.06623 | 6.62 | 1.63% | 0.11 | 6.7673 | 36.704 | 6.7673
SH Charging | J2376_POI - PANA_1 Ckt #1 138 kV | 138 | 11.5 | 357 | AMIL | J2694POI - COFFEN-N 345 1 | 140.15 | 57.77 | 65.48 | -0.65478 | 65.48 | 100% | 19.55 | 4.255 | 19.55 | 19.55
SH Charging | ISHI - HERRICK_TAP Ckt #1 69.0 kV | 69 | 6.6 | 357 | AMIL | P22:138:AMIL::PANA:1 | 108.21 | 44.09 | 11.75 | -0.11751 | 11.75 | 100% | 2.11 | 2.112 | 9.9 | 2.112
SH Charging | PANTHER - PANA_TAP Ckt #1 69.0 kV | 69 | 4.06 | 357 | AMIL | P22:138:AMIL::PANA:1 | 114.25 | 49.93 | 11.75 | -0.11751 | 11.75 | 100% | 1.3 | 1.2992 | 6.09 | 1.2992
SH Charging | LAKEWOOD - HERRICK_TAP Ckt #1 69.0 kV | 69 | 2.5 | 357 | AMIL | P22:138:AMIL::PANA:1 | 111.12 | 46.93 | 11.75 | -0.11751 | 11.75 | 100% | 0.8 | 0.8 | 3.75 | 0.8
SH Charging | LAKEWOOD - PANA_TAP Ckt #1 69.0 kV | 69 | 12 | 357 | AMIL | P22:138:AMIL::PANA:1 | 114.13 | 49.89 | 11.75 | -0.11751 | 11.75 | 100% | 3.84 | 3.84 | 18 | 3.84

## J2377
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | MCLEAN_R - PONTIAC_R Ckt #1 345 kV | 345 | 10.39 | 222 | CE | P12:COMED345:L8002::S:SRT:A_Dup1 | 120.64 | 73.04 | 134.03 | 0.21943 | 67.01 | 50% | 3.06 | 6.1301 | 33.248 | 6.1301
Summer Peak | DRESDEN_R - AD1-133_TAP Ckt #1 345 kV | 345 | 20.14 | 222 | CE | Base Case | 115.88 | 82.12 | 154.12 | 0.09138 | 27.91 | 18.11% | 2.15 | 11.8826 | 64.448 | 11.8826
Summer Peak | LORETTO_B - AD1-100_TAP Ckt #1 345 kV | 345 | 20 | 222 | CE | Base Case | 104.42 | 62.25 | 407.06 | 0.12572 | 38.39 | 9.43% | 1.11 | 11.8 | 64 | 11.8
Summer Peak | LORETTO_B - PONTIAC_B Ckt #1 345 kV | 345 | 11.47 | 222 | CE | Base Case | 102.11 | 59.9 | 407.06 | 0.12572 | 38.39 | 9.43% | 0.64 | 6.7673 | 36.704 | 6.7673

## J2379
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | J3076_POI - GIBSON Ckt #1 345 kV | 345 | 13.7 | 357/208 | AMIL/DEI | Base Case | 159.75 | 12.27 | 1851.62 | 0.0798 | 16.28 | 0.88% | 0.39 | 8.083 | 43.84 | 43.84
Summer Peak | SIOUX - ROXFORD Ckt #1 345 kV | 345 | 12.7 | 356/357 | AMMO/AMIL | Base Case | 147.4 | 24.79 | 837.77 | 0.06633 | 13.53 | 1.62% | 0.66 | 7.493 | 40.64 | 40.64
Summer Peak | J2662_POI - CASEY Ckt #1 345 kV | 345 | 2.5 | 357 | AMIL | J3076POI - GIBSON 345 kV ckt 1 | 136.42 | 19.29 | 758.72 | 0.40083 | 81.77 | 10.78% | 0.86 | 1.475 | 8 | 8
Summer Peak | JEFRSO - ROCKPT Ckt #1 765 kV | 765 | 110 | 205 | AEP | Base Case | 113.92 | 111.18 | 479.1 | 0.08065 | 16.45 | 3.43% | 4.12 | 119.9 | 119.9 | 119.9
Summer Peak | J2662_POI - NEWTON Ckt #1 345 kV | 345 | 24.04 | 357 | AMIL | J3076POI - GIBSON 345 kV ckt 1 | 103.23 | 19.18 | 439.74 | 0.40283 | 82.18 | 18.69% | 2.65 | 14.1836 | 76.928 | 14.1836
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | J1266_POI - WSALEM_1 Ckt #1 138 kV | - | 2.26 | 138 | 264 | 701/357 | central prior queud/AMIL | J2033 POI - XENIA 345 kV ckt 1 | 187.98 | 123.47 | 372.79 | 6.1% | 12.2 | 266.45 | 0.836 | 3.842 | 4.58% | 0.176
NRIS | J3130_POI - J1266_POI Ckt #1 138 kV | 1.98 | - | 138 | 240 | 701/357 | central prior queud/AMIL | J1241 POI - MTVERNW 345 kV ckt 1 | 204.96 | 123.34 | 368.56 | 6.1% | 12.2 | 266.45 | 0.733 | 3.366 | 4.58% | 0.154
NRIS | KINMUNDY_S - J3130_POI Ckt #1 138 kV | 6.09 | - | 138 | 240 | 357 | AMIL | J1241 POI - MTVERNW 345 kV ckt 1 | 186.04 | 123.82 | 322.68 | 6.1% | 12.2 | 220.57 | 2.253 | 10.353 | 5.53% | 0.571
NRIS | J3224_POI - KINMUNDY_S Ckt #1 138 kV | 20.31 | - | 138 | 175 | 357 | AMIL | J2033 POI - XENIA 345 kV ckt 1 | 100.73 | 20.24 | 160.33 | 9.68% | 19.35 | 114.54 | 7.515 | 34.527 | 16.89% | 1.269
NRIS | J1422_POI - ALBION_N Ckt #1 138 kV | - | 5.87 | 138 | 192 | 357 | AMIL | J1241 POI - MTVERNW 345 kV ckt 1 | 119.52 | -45.74 | 275.22 | 6.62% | 13.23 | 97.86 | 2.172 | 9.979 | 13.52% | 0.294
NRIS | TANNER - J3224_POI Ckt #1 138 kV | 7.29 | - | 138 | 175 | 357 | AMIL | J1241 POI - MTVERNW 345 kV ckt 1 | 119.41 | 20.14 | 188.84 | 9.73% | 19.45 | 70.8 | 2.697 | 12.393 | 27.47% | 0.741
NRIS | MTVERNW - ASHLEY Ckt #1 138 kV | 12.17 | - | 138 | 202 | 357 | AMIL | J1241 POI - MTVERNW 345 kV ckt 1 | 103.66 | 43.99 | 167.06 | 5.19% | 10.39 | 107.24 | 4.503 | 20.689 | 9.69% | 0.436

## J2383
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | DRESDEN_R - AD1-133_TAP Ckt #1 345 kV | 345 | 20.14 | 222 | CE | Base Case | 115.88 | 82.12 | 154.12 | 0.05088 | 5.19 | 3.37% | 0.4 | 11.8826 | 64.448 | 11.8826
Summer Peak | JEFRSO - ROCKPT Ckt #1 765 kV | 765 | 110 | 205 | AEP | Base Case | 113.92 | 111.18 | 479.1 | 0.06389 | 6.52 | 1.36% | 1.63 | 119.9 | 119.9 | 119.9
Summer Peak | LORETTO_B - AD1-100_TAP Ckt #1 345 kV | 345 | 20 | 222 | CE | Base Case | 104.42 | 62.25 | 407.06 | 0.06737 | 6.87 | 1.69% | 0.2 | 11.8 | 64 | 11.8
Summer Peak | LORETTO_B - PONTIAC_B Ckt #1 345 kV | 345 | 11.47 | 222 | CE | Base Case | 102.11 | 59.9 | 407.06 | 0.06737 | 6.87 | 1.69% | 0.11 | 6.7673 | 36.704 | 6.7673

## J2402
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | J3076_POI - GIBSON Ckt #1 345 kV | 345 | 13.7 | 357/208 | AMIL/DEI | Base Case | 159.75 | 12.27 | 1851.62 | 0.16509 | 33.68 | 1.82% | 0.8 | 8.083 | 43.84 | 43.84
Summer Peak | ASTER - PR_STATE Ckt #1 345 kV | 345 | 7.2 | 357 | AMIL | Base Case | 106.78 | 64.69 | 1250.84 | 0.07966 | 16.25 | 1.3% | 0.06 | 4.248 | 23.04 | 4.248
Summer Peak | J2662_POI - CASEY Ckt #1 345 kV | 345 | 2.5 | 357 | AMIL | Base Case | 104.12 | 21.71 | 1475.29 | 0.07521 | 15.34 | 1.04% | 0.02 | 1.475 | 8 | 1.475
Summer Peak | FRANKLIN - AKINTP Ckt #1 138 kV | 138 | 5.28 | 361 | SIPC | W_FRFT_E - NORRIS 345 1 | 100.36 | 35.67 | 47.36 | 0.05075 | 10.35 | 21.85% | 0.43 | 1.9536 | 8.976 | 1.9536

## J2413
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | LORETTO_B - AD1-100_TAP Ckt #1 345 kV | 345 | 20 | 222 | CE | Base Case | 104.42 | 62.25 | 407.06 | 0.05736 | 8.78 | 2.16% | 0.25 | 11.8 | 64 | 11.8
Summer Peak | LORETTO_B - PONTIAC_B Ckt #1 345 kV | 345 | 11.47 | 222 | CE | Base Case | 102.11 | 59.9 | 407.06 | 0.05736 | 8.78 | 2.16% | 0.15 | 6.7673 | 36.704 | 6.7673
Summer Peak | J2809_POI - GILMAN Ckt #1 138 kV | 138 | 7.6 | 357 | AMIL | Base Case | 109.65 | 8.39 | 278.57 | 0.0837 | 12.81 | 4.6% | 0.13 | 2.812 | 12.92 | 2.812
SH Charging | GOOS_CRK - RISING Ckt #1 345 kV | 345 | 14.6 | 357 | AMIL | Base Case | 100.78 | 59.27 | 225.91 | -0.12763 | 19.14 | 8.47% | 0.73 | 8.614 | 46.72 | 8.614
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate($MM)
NRIS | HOOPESTN_N - PAXTON_E_N Ckt #1 138 kV | 20.88 | - | 138 | 325 | 357 | AMIL | P12:345:AMIL::CLINTON:BROKAW:4535 | 135.08 | 0.02 | 438.99 | 58.79% | 88.19 | 264.57 | 7.726 | 35.496 | 33.33% | 11.831
NRIS | J2809_POI - GILMAN Ckt #1 138 kV | 7.6 | - | 138 | 255 | 357 | AMIL | BROKAW - TAZEWELL 345 kV ckt 1 | 154.52 | 67.07 | 326.97 | 8.56% | 12.85 | 286.4 | 2.812 | 12.92 | 4.49% | ER Upgrade
NRIS | J2565_POI - J2809_POI Ckt #1 138 kV | - | 0.025 | 138 | 255 | 357 | AMIL | BROKAW - TAZEWELL 345 kV ckt 1 | 125.15 | 67.27 | 251.86 | 8.56% | 12.85 | 211.28 | 0.00925 | 0.0425 | 6.08% | 0.00056

## J2426
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | J3076_POI - GIBSON Ckt #1 345 kV | 345 | 13.7 | 357/208 | AMIL/DEI | Base Case | 159.75 | 12.27 | 1851.62 | 0.07269 | 14.83 | 0.8% | 0.35 | 8.083 | 43.84 | 43.84
Summer Peak | J1266_POI - J3130_POI Ckt #1 138 kV | 138 | 1.98 | 701/357 | CLASSIC PQ/AMIL | J3224POI - TANNER 138 kV ckt 1 | 138.03 | 20.82 | 415.7 | 0.48836 | 99.63 | 23.97% | 0.81 | 0.7326 | 3.366 | 3.366
Summer Peak | J1266_POI - WSALEM_1 Ckt #1 138 kV | 138 | 3.15 | 701/357 | CLASSIC PQ/AMIL | J3224POI - TANNER 138 kV ckt 1 | 130.97 | 57.06 | 415.63 | 0.48828 | 99.61 | 23.97% | 0.28 | 1.1655 | 5.355 | 1.1655
Summer Peak | J2662_POI - CASEY Ckt #1 345 kV | 345 | 2.5 | 357 | AMIL | Base Case | 104.12 | 21.71 | 1475.29 | 0.15838 | 32.31 | 2.19% | 0.03 | 1.475 | 8 | 1.475
Summer Peak | J2794_POI - OTEGO Ckt #1 138 kV | 138 | 12.33 | 357 | AMIL | J3224POI - TANNER 138 kV ckt 1 | 143.94 | 35.69 | 332.63 | 0.4458 | 90.94 | 27.34% | 5.73 | 4.5621 | 20.961 | 20.961
Summer Peak | J2794_POI - KINMUNDY_N Ckt #1 138 kV | 138 | 3.43 | 357 | AMIL | J3224POI - TANNER 138 kV ckt 1 | 105.28 | 35.7 | 287.4 | 0.44625 | 91.04 | 31.68% | 0.4 | 1.2691 | 5.831 | 1.2691
Summer Peak | J3224_POI - KINMUNDY_S Ckt #1 138 kV | 138 | 20.31 | 357 | AMIL | P22:138:AMIL::RAMSEYEAST:1 | 150.76 | 56.85 | 321.93 | 0.44449 | 90.68 | 28.17% | 9.73 | 7.5147 | 34.527 | 34.527
Summer Peak | J3224_POI - TANNER Ckt #1 138 kV | 138 | 7.29 | 357 | AMIL | P22:138:AMIL::RAMSEYEAST:1 | 237.85 | 56.85 | 441.37 | 0.44332 | 90.44 | 20.49% | 2.54 | 2.6973 | 12.393 | 12.393
Summer Peak | JEFRSO - ROCKPT Ckt #1 765 kV | 765 | 110 | 205 | AEP | Base Case | 113.92 | 111.18 | 479.1 | 0.07009 | 14.3 | 2.98% | 3.58 | 119.9 | 119.9 | 119.9
Summer Peak | SIOUX - ROXFORD Ckt #1 345 kV | 345 | 12.7 | 356/357 | AMMO/AMIL | Base Case | 147.4 | 24.79 | 837.77 | 0.07491 | 15.28 | 1.82% | 0.74 | 7.493 | 40.64 | 40.64
Summer Peak | OTEGO - RAMSEY_CIPS Ckt #1 138 kV | 138 | 11.9 | 357 | AMIL | J3224POI - TANNER 138 kV ckt 1 | 147.54 | 56.34 | 429.88 | 0.44435 | 90.65 | 21.09% | 4.27 | 4.403 | 20.23 | 20.23
Summer Peak | SNDVLSW - SANDV_TP Ckt #1 69.0 kV | 69 | 6.83 | 357 | AMIL | J3224POI - TANNER 138 kV ckt 1 | 124.41 | 59.91 | 38.62 | 0.06883 | 14.04 | 36.35% | 0.79 | 2.1856 | 10.245 | 2.1856
SH Charging | OTEGO - RAMSEY_CIPS Ckt #1 138 kV | 138 | 11.9 | 357 | AMIL | Base Case | 120.02 | 54.29 | 109.67 | -0.30886 | 61.77 | 56.32% | 2.48 | 4.403 | 20.23 | 4.403
SH Charging | J3224_POI - TANNER Ckt #1 138 kV | 138 | 7.29 | 357 | AMIL | P12:138:AMIL::OTEGO:RAMSEY-E:1653 | 109.84 | 37.48 | 124.23 | -0.4458 | 89.16 | 71.77% | 1.94 | 2.6973 | 12.393 | 2.6973
SH Charging | J3224_POI - KINMUNDY_S Ckt #1 138 kV | 138 | 20.31 | 357 | AMIL | P12:138:AMIL::OTEGO:RAMSEY-E:1653 | 108.78 | 37.4 | 124.4 | -0.44638 | 89.28 | 71.77% | 5.39 | 7.5147 | 34.527 | 7.5147
SH Charging | J2425_POI - ROOTBEER Ckt #1 345 kV | 345 | 13.16 | 330/356 | AECI/AMMO | Base Case | 115.09 | NA | 145.03 | -0.05021 | 10.04 | 6.92% | 0.54 | 7.7644 | 42.112 | 7.7644
SH Charging | J2425_POI - ENON_TP Ckt #1 345 kV | 345 | 5.79 | 330/356 | AECI/AMMO | Base Case | 114.99 | 84.43 | 145.03 | -0.05021 | 10.04 | 6.92% | 0.24 | 3.4161 | 18.528 | 3.4161
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | J3224_POI - TANNER Ckt #1 138 kV | 7.29 | - | 138 | 175 | 357 | AMIL | P12:345:AMIL-CE::BROKAW:MTPULASKI:18806 | 204.98 | 4.61 | 354.1 | 31.51% | 63.01 | 294.35 | 2.6973 | 12.393 | 21.41% | ER upgrade
NRIS | J1266_POI - WSALEM_1 Ckt #1 138 kV | - | 2.26 | 138 | 264 | 701/357 | central prior queud/AMIL | J2033 POI - XENIA 345 kV ckt 1 | 187.98 | 123.47 | 372.79 | 34.04% | 68.08 | 266.45 | 0.836 | 3.842 | 25.55% | ER upgrade
NRIS | J3130_POI - J1266_POI Ckt #1 138 kV | 1.98 | - | 138 | 240 | 701/357 | central prior queud/AMIL | J2033 POI - XENIA 345 kV ckt 1 | 186.26 | 123.48 | 323.55 | 34.04% | 68.08 | 266.45 | 0.7326 | 3.366 | 25.55% | ER upgrade
NRIS | KINMUNDY_S - J3130_POI Ckt #1 138 kV | 6.09 | - | 138 | 240 | 357 | AMIL | J2033 POI - XENIA 345 kV ckt 1 | 167.35 | 123.96 | 277.67 | 34.04% | 68.08 | 220.57 | 2.2533 | 10.353 | 30.87% | ER upgrade
NRIS | KINMUNDY_S - J3224_POI Ckt #1 138 kV | 20.31 | - | 138 | 175 | 357 | AMIL | P12:345:AMIL-CE::BROKAW:MTPULASKI:18806 | 142.22 | 4.66 | 244.22 | 31.56% | 63.12 | 184.17 | 7.5147 | 34.527 | 34.27% | ER upgrade
NRIS | KINMUNDY_N - J2794_POI Ckt #1 138 kV | 3.43 | - | 138 | 240 | 357 | AMIL | J2747POI - EDWDSP 345 kV ckt 1 | 103.35 | 42.36 | 206.91 | 30.84% | 61.68 | 166.93 | 1.2691 | 5.831 | 36.95% | ER upgrade

## J2532
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Cont Name | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | DRESDEN_R - AD1-133_TAP Ckt #1 345 kV | 345 | 20.14 | 222 | CE | Base Case | 115.88 | 82.12 | 154.12 | 0.09427 | 19.23 | 12.48% | 1.48 | 11.8826 | 64.448 | 11.8826
Summer Peak | BLUEMOUND_B - PONTIAC_B Ckt #1 345 kV | 345 | 27.35 | 222 | CE | P4:COMEDBRO:45:BT3:4:SRT:A | 110.46 | 72.05 | 44.99 | 0.22054 | 44.99 | 100% | 16.14 | 16.1365 | 87.52 | 16.1365
Summer Peak | LORETTO_B - AD1-100_TAP Ckt #1 345 kV | 345 | 20 | 222 | CE | Base Case | 104.42 | 62.25 | 407.06 | 0.12616 | 25.74 | 6.32% | 0.75 | 11.8 | 64 | 11.8
Summer Peak | LORETTO_B - PONTIAC_B Ckt #1 345 kV | 345 | 11.47 | 222 | CE | Base Case | 102.11 | 59.9 | 407.06 | 0.12616 | 25.74 | 6.32% | 0.43 | 6.7673 | 36.704 | 6.7673

## J2536
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | MAZON_R - AD2-066_TAP Ckt #1 138 kV | 138 | 6.14 | 222 | CE | Base Case | 115.88 | 56.95 | 73.61 | 0.16215 | 33.08 | 44.94% | 1.02 | 2.2718 | 10.438 | 2.2718
Summer Peak | DRESDEN_R - ESS_J339_R Ckt #1 138 kV | 138 | 2.9 | 222 | CE | Base Case | 104.75 | 59.76 | 66.49 | 0.14622 | 29.83 | 44.86% | 0.48 | 1.073 | 4.93 | 1.073
Summer Peak | CHANNAHON_R - MAZON_R Ckt #1 138 kV | 138 | 10.02 | 222 | CE | Base Case | 101.5 | 47.06 | 66.49 | 0.14622 | 29.83 | 44.86% | 1.66 | 3.7074 | 17.034 | 3.7074
SH Charging | CORBIN - AF2-128_TAP Ckt #1 138 kV | 138 | 4.33 | 357/720 | AMIL/Are_720 | Base Case | 106.84 | 63.68 | 32.61 | -0.1219 | 24.38 | 74.76% | 1.2 | 1.6021 | 7.361 | 1.6021

## J2551
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | MAZON_R - AD2-066_TAP Ckt #1 138 kV | 138 | 6.14 | 222 | CE | Base Case | 115.88 | 56.95 | 73.61 | 0.12041 | 13.51 | 18.35% | 0.42 | 2.2718 | 10.438 | 2.2718
Summer Peak | DRESDEN_R - ESS_J339_R Ckt #1 138 kV | 138 | 2.9 | 222 | CE | Base Case | 104.75 | 59.76 | 66.49 | 0.10893 | 12.22 | 18.38% | 0.2 | 1.073 | 4.93 | 1.073
Summer Peak | CHANNAHON_R - MAZON_R Ckt #1 138 kV | 138 | 10.02 | 222 | CE | Base Case | 101.5 | 47.06 | 66.49 | 0.10893 | 12.22 | 18.38% | 0.68 | 3.7074 | 17.034 | 3.7074
SH Charging | KEWANEE_23 - PUTNAM Ckt #1 138 kV | 138 | 30.6 | 222/357 | CE/AMIL | P23:138:AMIL::BUREAU:H7 | 110.71 | 48.34 | 23.16 | -0.21051 | 23.16 | 100% | 11.32 | 11.322 | 52.02 | 11.322
SH Charging | CORBIN - AF2-128_TAP Ckt #1 138 kV | 138 | 4.33 | 357/720 | AMIL/Are_720 | Base Case | 106.84 | 63.68 | 32.61 | -0.07486 | 8.23 | 25.24% | 0.4 | 1.6021 | 7.361 | 1.6021
SH Charging | AF2-128_TAP - AG1-005_TAP Ckt #1 138 kV | 138 | 2.67 | 720/222 | Are_720/CE | Base Case | 98.96 | 57.14 | 32.61 | -0.07486 | 8.23 | 25.24% | 0.25 | 0.9879 | 4.539 | 0.9879

## J2552
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact (Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | QUAD_1_3-11 - ROCK_CK3 Ckt #1 345 kV | 345 | 5 | 222/627 | CE/ALTW | P55:161:MEC:HILLS:8T1 8T2:DIFF | 126.26 | 111.33 | 91.38 | 0.2099 | 27.29 | 29.86% | 0.88 | 2.95 | 16 | 2.95
Summer Peak | ELECT_JCT_B - LOMBARD_B Ckt #1 345 kV | 345 | 17.64 | 222 | CE | Base Case | 107.48 | 98.87 | 21.95 | 0.05043 | 6.56 | 29.89% | 3.11 | 10.4076 | 56.448 | 10.4076
SH Charging | QUAD_8-10 - MEC_CORDOVA3 Ckt #1 345 kV | 345 | 2.22 | 222/635 | CE/MEC | P611:345-345:CE:CORDOVA:QUAD:1:QUAD:ESS H471:1 | 190.52 | 114.1 | 85.04 | -0.38582 | 50.16 | 58.98% | 4.19 | 1.3098 | 7.104 | 7.104

## J2575
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | KOCH - CINCNATI Ckt #1 69.0 kV | 69 | 1.67 | 357 | AMIL | P23:138:AMIL::TOWERLINE:H3 | 105.81 | 53.82 | 33.3 | 0.16487 | 33.3 | 100% | 0.53 | 0.5344 | 2.505 | - | 0.5344
Summer Peak | MIDWEST - PEKIN_ENERG Ckt #1 69.0 kV | 69 | 0.06 | 357 | AMIL | P23:138:AMIL::TOWERLINE:H11 | 161 | 94.63 | 21.23 | 0.10514 | 21.23 | 100% | 0.09 | 0.0192 | 0.09 | - | 0.09
Summer Peak | MIDWEST - GROB_TAP Ckt #1 69.0 kV | 69 | 0.99 | 357 | AMIL | P23:138:AMIL::TOWERLINE:H11 | 147.26 | 87.01 | 21.23 | 0.10514 | 21.23 | 100% | 1.49 | 0.3168 | 1.485 | - | 1.485
Summer Peak | COURT - COURT_TAP Ckt #1 69.0 kV | 69 | 0.1 | 357 | AMIL | P23:138:AMIL::TOWERLINE:H11 | 137.67 | 81.45 | 21.23 | 0.10514 | 21.23 | 100% | 0.15 | 0.032 | 0.15 | - | 0.15
Summer Peak | COURT - GROB_TAP Ckt #1 69.0 kV | 69 | 0.48 | 357 | AMIL | P23:138:AMIL::TOWERLINE:H11 | 145.32 | 85.71 | 21.23 | 0.10514 | 21.23 | 100% | 0.72 | 0.1536 | 0.72 | - | 0.72
Summer Peak | CINCY_TAP - EDWARDS1 Ckt #1 69.0 kV | 69 | 0.97 | 357 | AMIL | P23:138:AMIL::TOWERLINE:H11 | 155.95 | 88.65 | 29.42 | 0.14567 | 29.42 | 100% | 1.46 | 0.3104 | 1.455 | - | 1.455
Summer Peak | CINCY_TAP - CINCNATI Ckt #1 69.0 kV | 69 | 3.67 | 357 | AMIL | P23:138:AMIL::TOWERLINE:H11 | 148.06 | 87.01 | 29.42 | 0.14567 | 29.42 | 100% | 5.51 | 1.1744 | 5.505 | - | 5.505
Summer Peak | WHLR_45TAP - COURT_TAP Ckt #1 69.0 kV | 69 | 2.07 | 357 | AMIL | P23:138:AMIL::TOWERLINE:H11 | 127.2 | 75.25 | 21.23 | 0.10514 | 21.23 | 100% | 0.66 | 0.6624 | 3.105 | - | 0.6624
Summer Peak | WHLR_45TAP - EDWARDS1 Ckt #1 69.0 kV | 69 | 0.32 | 357 | AMIL | P23:138:AMIL::TOWERLINE:H11 | 127.16 | 75.19 | 21.23 | 0.10514 | 21.23 | 100% | 0.1 | 0.1024 | 0.48 | - | 0.1024
Summer Peak | 2CINCNATI - 4CINCINATTI Xfmr #2 138 kV | 138/69 | - | 357 | AMIL | P23:138:AMIL::CINCINNATI:H3 | 213.88 | 56.3 | 164.33 | 0.48727 | 98.41 | 59.89% | 4.19 | - | - | 7 | 7
Summer Peak | 4TOWERLINE - 4TAZEWELL Ckt #1 138 kV | 138 | 6.22 | 357 | AMIL | BROKAW - TAZEWELL 345 kV ckt 1 | 104.63 | 60.9 | 66.44 | 0.32898 | 66.44 | 100% | 2.3 | 2.3014 | 10.574 | - | 2.3014
Summer Peak | 4CINCINATTI - 2CINCNATI Xfmr #1 69.0 kV | 138/69 | - | 357 | AMIL | P23:138:AMIL::CINCINNATI:H5 | 224.26 | 56.3 | 164.33 | 0.48727 | 98.41 | 59.89% | 4.19 | - | - | 7 | 7
SH Charging | GRAND_ISLND - TOPEKA Ckt #1 69.0 kV | 69 | 6.13 | 357 | AMIL | J3003POI - HAVANA2 138 V ckt 1 | 103.92 | 59.01 | 12.74 | -0.06435 | 12.74 | 100% | 1.96 | 1.9616 | 9.195 | - | 1.9616

## J2607
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | SIOUX - ROXFORD Ckt #1 345 kV | 345 | 12.7 | 356/357 | AMMO/AMIL | Base Case | 147.4 | 24.79 | 837.77 | 0.10162 | 20.74 | 2.48% | 1.01 | 7.493 | 40.64 | - | 40.64
Summer Peak | JEFRSO - ROCKPT Ckt #1 765 kV | 765 | 110 | 205 | AEP | Base Case | 113.92 | 111.18 | 479.1 | 0.05969 | 12.18 | 2.54% | 3.05 | 119.9 | 119.9 | - | 119.9
Summer Peak | LORETTO_B - AD1-100_TAP Ckt #1 345 kV | 345 | 20 | 222 | CE | Base Case | 104.42 | 62.25 | 407.06 | 0.05238 | 10.68 | 2.62% | 0.31 | 11.8 | 64 | - | 11.8
Summer Peak | LORETTO_B - PONTIAC_B Ckt #1 345 kV | 345 | 11.47 | 222 | CE | Base Case | 102.11 | 59.9 | 407.06 | 0.05238 | 10.68 | 2.62% | 0.18 | 6.7673 | 36.704 | - | 6.7673
Summer Peak | MORO - LACLEDE_NTP Ckt #1 138 kV | 138 | 7.07 | 357 | AMIL | P71:138-345:AMIL::COFFEEN:ROXFORD:51:WOODRIVER:ROXFORD:02 | 120.93 | 95.7 | 107.27 | 0.26661 | 54.38 | 50.69% | 1.33 | 2.6159 | 12.019 | - | 2.6159
SH Charging | J2694_POI - COFFEN-N Ckt #1 345 kV | 345 | 8 | 357 | AMIL | P23:138-345:AMIL::FARADAY:1 | 125.01 | 66.04 | 333.81 | -0.26177 | 52.36 | 15.69% | 0.74 | 4.72 | 25.6 | - | 4.72
SH Charging | J2425_POI - ROOTBEER Ckt #1 345 kV | 345 | 13.16 | 330/356 | AECI/AMMO | Base Case | 115.09 | NA | 145.03 | -0.05652 | 11.3 | 7.79% | 0.6 | 7.7644 | 42.112 | - | 7.7644
SH Charging | J2425_POI - ENON_TP Ckt #1 345 kV | 345 | 5.79 | 330/356 | AECI/AMMO | Base Case | 114.99 | 84.43 | 145.03 | -0.05652 | 11.3 | 7.79% | 0.27 | 3.4161 | 18.528 | - | 3.4161

## J2627
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact (Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | 2HAMLTNAM - 4HAMLTNAM Xfmr #1 138 kV | 138/69 | - | 357 | AMIL | P22:161:AECI:5PALMYR_AI:11 | 184.96 | 137.03 | 13.18 | 0.08616 | 13.18 | 100% | 7 | - | - | 7 | 7
Summer Peak | J2627_SUB - 4E_QUINCY_S Ckt #1 138 kV | 138 | 1.17 | 801/357 | CLASSIC STUD/AMIL | Base Case | 107.14 | 0 | 152.76 | 0.99844 | 152.76 | 100% | 0.43 | 0.4329 | 1.989 | - | 0.4329
SH Charging | 5PALMYR_AI - 7PALMYR_AI Xfmr #1 345 kV | 345/161 | - | 330 | AECI | P23:345:AMIL::HERLEMAN:V13 | 122.71 | 72.3 | 74.92 | -0.30359 | 45.54 | 60.78% | 6.08 | - | - | 10 | 10
SH Charging | VIELE161 - _DENMARK5 Ckt #1 161 kV | 161 | 13.1 | 627 | ALTW | P23:345:AMMO::MAYWOOD:V43 | 120.72 | 45.21 | 41.57 | -0.07816 | 11.72 | 28.19% | 1.37 | 4.847 | 22.27 | - | 4.847

## J2647
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | J3076_POI - GIBSON Ckt #1 345 kV | 345 | 13.7 | 357/208 | AMIL/DEI | P23:138-345:AMIL::KANSAS:V23 | 186.64 | 7.8 | 966.13 | 0.26274 | 80.4 | 8.32% | 3.65 | 8.083 | 43.84 | - | 43.84
Summer Peak | SIOUX - ROXFORD Ckt #1 345 kV | 345 | 12.7 | 356/357 | AMMO/AMIL | Base Case | 147.4 | 24.79 | 837.77 | 0.05667 | 17.34 | 2.07% | 0.84 | 7.493 | 40.64 | - | 40.64
Summer Peak | J2662_POI - CASEY Ckt #1 345 kV | 345 | 2.5 | 357 | AMIL | Base Case | 104.12 | 21.71 | 1475.29 | 0.10047 | 30.74 | 2.08% | 0.03 | 1.475 | 8 | - | 1.475
Summer Peak | J3076_POI - ALBION Ckt #1 345 kV | 345 | 4.66 | 357 | AMIL | J3076POI 345 - J3076SUB 345 1 | 101.9 | NA | 295.54 | 0.24503 | 74.98 | 25.37% | 0.7 | 2.7494 | 14.912 | - | 2.7494
Summer Peak | FRANKLIN - AKINTP Ckt #1 138 kV | 138 | 5.28 | 361 | SIPC | 7W_FRFT_E 345 - 7NORRIS 345 1 | 100.36 | 35.67 | 47.36 | 0.07008 | 21.44 | 45.27% | 0.88 | 1.9536 | 8.976 | - | 1.9536

## J2724
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact (Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | SIOUX - ROXFORD Ckt #1 345 kV | 345 | 12.7 | 356/357 | AMMO/AMIL | Base Case | 147.4 | 24.79 | 837.77 | 0.0616 | 18.84 | 2.25% | 0.91 | 7.493 | 40.64 | - | 40.64
Summer Peak | J1263_POI - KANSAS Ckt #1 345 kV | 345 | 13 | 701/357 | CLASSIC PQ/AMIL | P12:765:AEP:AEP ROCKP-AEP JEFF 765 ADJ ROCKP 400MW | 120.37 | 59.93 | 308.27 | 0.20005 | 61.22 | 19.86% | 1.52 | 7.67 | 41.6 | - | 7.67
Summer Peak | J1263_POI - CASEY Ckt #1 345 kV | 345 | 8 | 701/357 | CLASSIC PQ/AMIL | P12:765:AEP:AEP ROCKP-AEP JEFF 765 ADJ ROCKP 400MW | 116.21 | 34.12 | 309.42 | 0.20103 | 61.52 | 19.88% | 0.94 | 4.72 | 25.6 | - | 4.72
Summer Peak | JEFRSO - ROCKPT Ckt #1 765 kV | 765 | 110 | 205 | AEP | Base Case | 113.92 | 111.18 | 479.1 | 0.10332 | 31.62 | 6.6% | 7.91 | 119.9 | 119.9 | - | 119.9

## J2853
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | DRESDEN_R - AD1-133_TAP Ckt #1 345 kV | 345 | 20.14 | 222 | CE | Base Case | 115.88 | 82.12 | 154.12 | 0.05442 | 5.53 | 3.59% | 0.43 | 11.8826 | 64.448 | - | 11.8826
Summer Peak | LORETTO_B - AD1-100_TAP Ckt #1 345 kV | 345 | 20 | 222 | CE | Base Case | 104.42 | 62.25 | 407.06 | 0.08068 | 8.2 | 2.01% | 0.24 | 11.8 | 64 | - | 11.8
Summer Peak | LORETTO_B - PONTIAC_B Ckt #1 345 kV | 345 | 11.47 | 222 | CE | Base Case | 102.11 | 59.9 | 407.06 | 0.08068 | 8.2 | 2.01% | 0.14 | 6.7673 | 36.704 | - | 6.7673
Summer Peak | JACK_IND_S - JACKSNVL Ckt #1 138 kV | 138 | 7.36 | 357 | AMIL | Base Case | 109.49 | 91.59 | 108.01 | 0.08601 | 8.74 | 8.09% | 0.22 | 2.7232 | 12.512 | - | 2.7232
Summer Peak | QUIVER - MASON_IL Ckt #1 138 kV | 138 | 8.24 | 357 | AMIL | Base Case | 106.37 | 42.38 | 62 | 0.06489 | 6.6 | 10.65% | 0.32 | 3.0488 | 14.008 | - | 3.0488
Summer Peak | SPALDING - 4_PORTER Ckt #1 138 kV | 138 | 5.5 | 360 | CWLP | P23:138:CWLP:WESTCHESTER:WCB1 | 101.81 | 85.27 | 101.93 | 0.46824 | 47.6 | 46.7% | 0.95 | 2.035 | 9.35 | - | 2.035
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | J2963_POI - PURO Ckt #1 138 kV | 0.15 | - | 138 | 160 | 357 | AMIL | P12:345:AMIL-CE::BROKAW:MTPULASKI:18806 | 163.83 | 49.86 | 212.27 | 7.72% | 7.72 | 156.16 | 0.0555 | 0.255 | 4.944% | 0.0126
NRIS | SANJOSERAIL - TOWERLINE Ckt #1 138 kV | 13.6 | - | 138 | 305 | 357 | AMIL | P12:345:AMIL-CE::BROKAW:MTPULASKI:18806 | 149.18 | 95.5 | 359.5 | 5.99% | 5.99 | 57.51 | 5.032 | 23.12 | 10.42% | 2.4081
NRIS | J3005_POI - GILLETT Ckt #1 138 kV | 7.06 | - | 138 | 160 | 357 | AMIL | P12:345:ATC-ITC:W-19:HLV_345:HCKRYCK3:NLL | 157.01 | 0.73 | 250.5 | 7.17% | 7.17 | 120.06 | 2.6122 | 12.002 | 5.972% | 0.7168
NRIS | GILLETT - DOCKET Ckt #1 138 kV | 8.56 | - | 138 | 202 | 357 | AMIL | P12:138:CWLP:SPAULDING:WESTCHESTER:1 | 116.6 | -30.98 | 266.51 | 13.57% | 13.57 | 125.57 | 3.1672 | 14.552 | 10.81% | 0.3423
NRIS | SHOCKEY - J3005POI Ckt #1 138 kV | 1.83 | - | 138 | 160 | 357 | AMIL | P12:138:CWLP:SPAULDING:WESTCHESTER:1 | 127.87 | -1.36 | 205.94 | 8.4% | 8.4 | 74.72 | 0.6771 | 3.111 | 11.24% | 0.0761
NRIS | PURO - HAVANA3 Ckt #1 138 kV | 12 | - | 138 | 305 | 357 | AMIL | P12:345:AMIL-CE::BROKAW:MTPULASKI:18806 | 120.57 | 49.69 | 318.05 | 7.72% | 7.72 | 156.16 | 4.44 | 20.4 | 4.944% | 0.2195
NRIS | YATES - MERE_138 Ckt #1 138 kV | - | 19.3 | 138 | 159 | 357 | AMIL | P12:345:AMIL-CE::BROKAW:MTPULASKI:18806 | 110.32 | 36.96 | 138.46 | 5.93% | 5.93 | 85.55 | 7.141 | 32.81 | 6.932% | 0.495

## J2974
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | HULL - MARION2 Ckt #1 161 kV | 161 | 7 | 357/356 | AMIL/AMMO | P22:138:AMIL::HERLEMAN:1 | 125.99 | 25.01 | 162.46 | 0.70798 | 61.59 | 37.91% | 0.98 | 2.59 | 11.9 | - | 2.59
SH Charging | 5PALMYR_AI - 7PALMYR_AI Xfmr #1 345 kV | 345/161 | - | 330 | AECI | P23:345:AMIL::HERLEMAN:V13 | 122.71 | 72.3 | 74.92 | -0.34567 | 29.38 | 39.22% | 3.92 | - | - | 10 | 10
SH Charging | PALMYR_AI - HANW Ckt #1 161 kV | 161 | 9.43 | 330/356 | AECI/AMMO | J2972POI - HERLEMAN 138 kV ckt 1 | 113.62 | 60.95 | 39.07 | -0.4596 | 39.07 | 100% | 3.49 | 3.4891 | 16.031 | - | 3.4891
SH Charging | SPALDNG - HANW Ckt #1 161 kV | 161 | 6.92 | 330/356 | AECI/AMMO | J2972POI - HERLEMAN 138 kV ckt 1 | 108.2 | 58.7 | 39.07 | -0.4596 | 39.07 | 100% | 2.56 | 2.5604 | 11.764 | - | 2.5604
SH Charging | J2972_POI - HERLEMAN_1 Ckt #1 138 kV | 138 | 8.35 | 357 | AMIL | P22:345:AMMO::MONTGOMERY:A&B | NConv | 52.22 | 59.79 | -0.70343 | 59.79 | 100% | 14.2 | 3.0895 | 14.195 | - | 14.195
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | J1268_POI - AUBURNTP Ckt #1 161 kV | - | 7.39 | 161 | 224 | 356/330 | AMMO/AECI | P12:345:MEC:HILLS:SUB T-SUB 93:1:REACTOR | 141.13 | 82.7 | 233.43 | 7.12% | 6.05 | 41 | 2.7343 | 12.563 | 14.76% | 1.8538
NRIS | AUBURNTP - WINFIELD Ckt #1 161 kV | - | 8.98 | 161 | 224 | 330/356 | AMMO/AECI | P12:345:MEC:HILLS:SUB T-SUB 93:1:REACTOR | 140.9 | 82.19 | 233.43 | 7.12% | 6.05 | 41 | 3.3226 | 15.266 | 14.76% | 2.2527

## J2998
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | J3076POI - GIBSON 345 kV ckt 1 | 345 | 13.7 | 357/208 | AMIL/DEI | Base Case | 159.75 | 12.27 | 1851.62 | 0.0922 | 18.81 | 1.02% | 0.45 | 8.083 | 43.84 | - | 43.84
Summer Peak | SIOUX - ROXFORD 345 kV ckt 1 | 345 | 12.7 | 356/357 | AMMO/AMIL | Base Case | 147.4 | 24.79 | 837.77 | 0.11105 | 22.65 | 2.7% | 1.1 | 7.493 | 40.64 | - | 40.64
Summer Peak | CAHOKIA - TURKEY HILL 345 kV ckt 1 | 345 | 18.73 | 357 | AMIL | Base Case | 113.87 | 42.36 | 306.71 | 0.10293 | 21 | 6.85% | 0.76 | 11.0507 | 59.936 | - | 11.0507
Summer Peak | BALDWIN - BEEHIVE 345 kV ckt 1 | 345 | 31.16 | 357 | AMIL | Base Case | 109.12 | 48.72 | 262.78 | 0.0508 | 10.36 | 3.94% | 0.72 | 18.3844 | 99.712 | - | 18.3844
Summer Peak | ASTER - PR STATE 345 kV ckt 1 | 345 | 7.2 | 357 | AMIL | Base Case | 106.78 | 64.69 | 1250.84 | 0.14544 | 29.67 | 2.37% | 0.1 | 4.248 | 23.04 | - | 4.248
Summer Peak | J2662POI - CASEY 345 kV ckt 1 | 345 | 2.5 | 357 | AMIL | Base Case | 104.12 | 21.71 | 1475.29 | 0.07404 | 15.1 | 1.02% | 0.02 | 1.475 | 8 | - | 1.475
Summer Peak | CAHOK - CENTERV 138 kV ckt 1 | 138 | 6.09 | 357 | AMIL | Base Case | 161.41 | 57.92 | 63.09 | 0.10087 | 20.58 | 32.62% | 3.38 | 2.2533 | 10.353 | - | 10.353
Summer Peak | J3069POI - HERZOG 138 kV ckt 1 | 138 | 1.94 | 357 | AMIL | P12:345:AMIL::ASTER:PRAIRIESTATE:4513 | 153.58 | 95.59 | 175.04 | 0.62003 | 126.49 | 72.26% | 2.38 | 0.7178 | 3.298 | - | 3.298
Summer Peak | S BELLEVLLE - HERZOG 138 kV ckt 1 | 138 | 12.11 | 357 | AMIL | P12:345:AMIL::ASTER:PRAIRIESTATE:4513 | 137.09 | 84.13 | 100.02 | 0.35626 | 72.68 | 72.67% | 14.96 | 4.4807 | 20.587 | - | 20.587
Summer Peak | J3074POI - STEELEVLE N 138 kV ckt 1 | 138 | 2.56 | 357 | AMIL | Base Case | 133.41 | 24.62 | 202.69 | 0.07898 | 16.11 | 7.95% | 0.08 | 0.9472 | 4.352 | - | 0.9472
Summer Peak | J3069POI - FAYETTEVLLE 138 kV ckt 1 | 138 | 2.56 | 357 | AMIL | P12:345:AMIL::ASTER:PRAIRIESTATE:4513 | 133.23 | 95.6 | 126.56 | 0.62037 | 126.56 | 100% | 0.95 | 0.9472 | 4.352 | - | 0.9472
Summer Peak | BEL17 RING - S BELLEVLLE 138 kV ckt 1 | 138 | 2.57 | 357 | AMIL | Base Case | 123.8 | 65.74 | 66.86 | 0.10683 | 21.79 | 32.59% | 0.31 | 0.9509 | 4.369 | - | 0.9509
SH Charging | J2425POI - ROOTBEER 345 kV ckt 1 | 345 | 13.16 | 330/356 | AECI/AMMO | Base Case | 115.09 | NA | 145.03 | -0.08322 | 16.64 | 11.47% | 0.89 | 7.7644 | 42.112 | - | 7.7644
SH Charging | J2425POI - ENON_TP 345 kV ckt 1 | 345 | 5.79 | 330/356 | AECI/AMMO | Base Case | 114.99 | 84.43 | 145.03 | -0.08322 | 16.64 | 11.47% | 0.39 | 3.4161 | 18.528 | - | 3.4161
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | J3074POI - STEELEVLE N 138 kV ckt 1 | 2.2 | - | 138 | 160 | 357 | AMIL | J1306 POI - J3063POI 345 kV ckt 1 | 149.27 | 7.54 | 231.29 | 8.82% | 17.63 | 177.13 | 0.814 | 3.74 | 9.953% | ER Upgrade
NRIS | JORD - 4W_FRFT_E 138 kV ckt 1 | 6.45 | - | 138 | 478 | 357 | AMIL | P12:345:AMIL::MTVERNON-W:WESTFRANKFORT-E:4561 | 124.85 | 16.89 | 579.88 | 5.74% | 11.48 | 395.26 | 2.3865 | 10.965 | 2.904% | 0.0693
NRIS | J3069POI - HERZOG 138 kV ckt 1 | 1.94 | - | 138 | 338 | 357 | AMIL | J1306 POI - J3063POI 345 kV ckt 1 | 115.86 | 50.57 | 341.04 | 60.54% | 121.07 | 215.46 | 0.7178 | 3.298 | 56.19% | ER Upgrade
NRIS | FAYETTEVLLE - J3069POI 138 kV ckt 1 | 2.56 | - | 138 | 338 | 357 | AMIL | J1306 POI - J3063POI 345 kV ckt 1 | 101.15 | 50.72 | 293.21 | 60.54% | 121.07 | 167.63 | 0.9472 | 4.352 | 72.22% | ER Upgrade

## J3011
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | J3076POI - GIBSON 345 kV ckt 1 | 345 | 13.7 | 357/208 | AMIL/DEI | Base Case | 159.75 | 12.27 | 1851.62 | 0.09311 | 9.45 | 0.51% | 0.22 | 8.083 | 43.84 | - | 43.84
Summer Peak | J3011SUB - PR STATE 345 kV ckt 1 | 345 | 2.05 | 801/357 | CLASSIC STUD/AMIL | Base Case | 149.79 | 0 | 101.4 | 0.99899 | 101.4 | 100% | 6.56 | 1.2095 | 6.56 | - | 6.56
Summer Peak | SIOUX - ROXFORD 345 kV ckt 1 | 345 | 12.7 | 356/357 | AMMO/AMIL | Base Case | 147.4 | 24.79 | 837.77 | 0.11793 | 11.97 | 1.43% | 0.58 | 7.493 | 40.64 | - | 40.64
Summer Peak | J2691POI - RUSH 345 kV ckt 1 | 345 | 27 | 356 | AMMO | P23:345:AMIL::PRAIRIESTATE:V13 | 119.08 | 29.41 | 257.64 | 0.20861 | 21.17 | 8.22% | 1.31 | 15.93 | 86.4 | - | 15.93
Summer Peak | CAHOKIA - TURKEY HILL 345 kV ckt 1 | 345 | 18.73 | 357 | AMIL | Base Case | 113.87 | 42.36 | 306.71 | 0.05264 | 5.34 | 1.74% | 0.19 | 11.0507 | 59.936 | - | 11.0507
Summer Peak | BALDWIN - BEEHIVE 345 kV ckt 1 | 345 | 31.16 | 357 | AMIL | Base Case | 109.12 | 48.72 | 262.78 | 0.07658 | 7.77 | 2.96% | 0.54 | 18.3844 | 99.712 | - | 18.3844
Summer Peak | GATEWAY - PR STATE 345 kV ckt 1 | 345 | 43 | 357 | AMIL | Base Case | 105.63 | 0 | 357.7 | 0.1293 | 13.12 | 3.67% | 0.93 | 25.37 | 137.6 | - | 25.37
Summer Peak | J2662POI - CASEY 345 kV ckt 1 | 345 | 2.5 | 357 | AMIL | Base Case | 104.12 | 21.71 | 1475.29 | 0.08266 | 8.39 | 0.57% | 0.01 | 1.475 | 8 | - | 1.475
SH Charging | J3011SUB - PR STATE 345 kV ckt 1 | 345 | 2.05 | 801/357 | CLASSIC STUD/AMIL | Base Case | 168.53 | 0 | 100 | -0.99999 | 100 | 100% | 6.56 | 1.2095 | 6.56 | - | 6.56
SH Charging | J2425POI - ROOTBEER 345 kV ckt 1 | 345 | 13.16 | 330/356 | AECI/AMMO | Base Case | 115.09 | NA | 145.03 | -0.08309 | 8.31 | 5.73% | 0.44 | 7.7644 | 42.112 | - | 7.7644
SH Charging | J2425POI - ENON_TP 345 kV ckt 1 | 345 | 5.79 | 330/356 | AECI/AMMO | Base Case | 114.99 | 84.43 | 145.03 | -0.08309 | 8.31 | 5.73% | 0.2 | 3.4161 | 18.528 | - | 3.4161
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | JORD - 4W_FRFT_E 138 kV ckt 1 | 6.45 | - | 138 | 478 | 357 | AMIL | P12:345:AMIL::MTVERNON-W:WESTFRANKFORT-E:4561 | 124.85 | 16.89 | 579.88 | 6.2% | 6.2 | 395.26 | 2.3865 | 10.965 | 1.569% | 0.0374

## J3031
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | J3076POI - GIBSON 345 kV ckt 1 | 345 | 13.7 | 357/208 | AMIL/DEI | Base Case | 159.75 | 12.27 | 1851.62 | 0.13512 | 27.56 | 1.49% | 0.65 | 8.083 | 43.84 | - | 43.84
Summer Peak | SIOUX - ROXFORD 345 kV ckt 1 | 345 | 12.7 | 356/357 | AMMO/AMIL | Base Case | 147.4 | 24.79 | 837.77 | 0.07818 | 15.95 | 1.9% | 0.77 | 7.493 | 40.64 | - | 40.64
Summer Peak | GATEWAY - PR STATE 345 kV ckt 1 | 345 | 43 | 357 | AMIL | Base Case | 105.63 | 0 | 357.7 | 0.0536 | 10.93 | 3.06% | 0.78 | 25.37 | 137.6 | - | 25.37
Summer Peak | J2662POI - CASEY 345 kV ckt 1 | 345 | 2.5 | 357 | AMIL | Base Case | 104.12 | 21.71 | 1475.29 | 0.14864 | 30.32 | 2.06% | 0.03 | 1.475 | 8 | - | 1.475
Summer Peak | WLTNVLSH - WLTNVLTP 138 kV ckt 1 | 138 | 2.68 | 357 | AMIL | Base Case | 164.68 | 0.32 | 203.59 | 0.99797 | 203.59 | 100% | 4.56 | 0.9916 | 4.556 | - | 4.556
SH Charging | J2425POI - ROOTBEER 345 kV ckt 1 | 345 | 13.16 | 330/356 | AECI/AMMO | Base Case | 115.09 | NA | 145.03 | -0.05849 | 11.7 | 8.07% | 0.63 | 7.7644 | 42.112 | - | 7.7644
SH Charging | J2425POI - ENON_TP 345 kV ckt 1 | 345 | 5.79 | 330/356 | AECI/AMMO | Base Case | 114.99 | 84.43 | 145.03 | -0.05849 | 11.7 | 8.07% | 0.28 | 3.4161 | 18.528 | - | 3.4161
NRIS Results
Model | Monitored Facility | Line Length (miles) | Estimated Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | JORD - 4W_FRFT_E 138 kV ckt 1 | 6.45 | - | 138 | 478 | 357 | AMIL | P12:345:AMIL::MTVERNON-W:WESTFRANKFORT-E:4561 | 124.85 | 16.89 | 579.88 | 12.91% | 25.82 | 395.26 | 2.3865 | 10.965 | 0.065324 | 0.1559
NRIS | MTVERNW - ASHLEY 138 kV ckt 1 | 12.17 | - | 138 | 202 | 357 | AMIL | J2690POI - MTVERNW 345 kV ckt 1 | 103.66 | 43.99 | 167.06 | 9.58% | 19.15 | 107.24 | 4.5029 | 20.689 | 0.17857 | 0.8041

## J3200
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact(Harmers Only) | Dfax | MW Impact | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | J3076POI - GIBSON 345 kV ckt 1 | 345 | 13.7 | 357/208 | AMIL/DEI | Base Case | 159.75 | 12.27 | 1851.62 | 0.08283 | 21.12 | 1.14% | 0.5 | 8.083 | 43.84 | - | 43.84
Summer Peak | SIOUX - ROXFORD 345 kV ckt 1 | 345 | 12.7 | 356/357 | AMMO/AMIL | Base Case | 147.4 | 24.79 | 837.77 | 0.12947 | 33.02 | 3.94% | 1.6 | 7.493 | 40.64 | - | 40.64
Summer Peak | CAHOKIA - TURKEY HILL 345 kV ckt 1 | 345 | 18.73 | 357 | AMIL | P23:345:AMIL::PRAIRIESTATE:V13 | 133.98 | 41.68 | 101.79 | 0.39918 | 101.8 | 100% | 11.05 | 11.0507 | 59.936 | - | 11.0507
Summer Peak | CAHOKIA - GATEWAY 345 kV ckt 1 | 345 | 6.54 | 357 | AMIL | P23:345:AMIL::PRAIRIESTATE:V13 | 127.68 | 10.14 | 114.86 | 0.28372 | 72.34 | 62.98% | 2.43 | 3.8586 | 20.928 | - | 3.8586
Summer Peak | J2662POI - CASEY 345 kV ckt 1 | 345 | 2.5 | 357 | AMIL | Base Case | 104.12 | 21.71 | 1475.29 | 0.0682 | 17.4 | 1.18% | 0.02 | 1.475 | 8 | - | 1.475
SH Charging | CAHOK - CENTERV 138 kV ckt 1 | 138 | 6.09 | 357 | AMIL | P23:345:AMIL::TURKEYHILL:V9 | 118.8 | 39.84 | 75.39 | -0.30157 | 37.7 | 50.01% | 1.13 | 2.2533 | 10.353 | - | 2.2533
SH Charging | KREN - PORTR_RD 138 kV ckt 1 | 138 | 5.9 | 357 | AMIL | P23:345:AMIL::TURKEYHILL:V9 | 112.58 | 51.45 | 72.79 | -0.29114 | 36.39 | 49.99% | 1.09 | 2.183 | 10.03 | - | 2.183
SH Charging | J2425POI - ROOTBEER 345 kV ckt 1 | 345 | 13.16 | 330/356 | AECI/AMMO | Base Case | 115.09 | NA | 145.03 | -0.09092 | 11.37 | 7.84% | 0.61 | 7.7644 | 42.112 | - | 7.7644
SH Charging | J2425POI - ENON_TP 345 kV ckt 1 | 345 | 5.79 | 330/356 | AECI/AMMO | Base Case | 114.99 | 84.43 | 145.03 | -0.09092 | 11.37 | 7.84% | 0.27 | 3.4161 | 18.528 | - | 3.4161
NRIS Results
Model | Monitored Facility | Line Length (miles) | Voltage (kV) | Rating (MVA) | Areas | Areas Name | Contingency | Final AC %Loading | Base FG Flow | Top30 Impact | Dfax | MW Impact (MW) | Cumulative MW Impact (MW) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Cost Allocation (%) | Cost Estimate ($MM)
NRIS | JORD - 4W_FRFT_E 138 kV ckt 1 | 6.45 | 138 | 478 | 357 | AMIL | P12:345:AMIL::MTVERNON-W:WESTFRANKFORT-E:4561 | 124.85 | 16.89 | 579.88 | 5.46% | 13.66 | 395.26 | 2.3865 | 10.965 | 0.03456 | 0.0825

## J3216
ERIS Results
Model | Monitored Facility | kV | Line Length (miles) | Areas | Areas Name | Contingency | Final AC %Loading | Bench Final AC %Loading | Cumulative MW Impact (Harmers Only) | Dfax | MW Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM) | Reconductor Cost ($MM) | Rebuild Cost ($MM) | Replacement Cost ($MM) | Reinforcement Cost ($MM)
Summer Peak | MCLEAN - PONTIAC 345 kV ckt 1 | 345 | 10.39 | 222 | CE | P12:COMED345:L8002::S:SRT:A_Dup1 | 120.64 | 73.04 | 134.03 | 0.21943 | 67.01 | 50% | 3.06 | 6.1301 | 33.248 | - | 6.1301
Summer Peak | DRESDEN - AD1-133 TAP 345 kV ckt 1 | 345 | 20.14 | 222 | CE | Base Case | 115.88 | 82.12 | 154.12 | 0.09138 | 27.91 | 18.11% | 2.15 | 11.8826 | 64.448 | - | 11.8826
Summer Peak | LORETTO - AD1-100 TAP 345 kV ckt 1 | 345 | 20 | 222 | CE | Base Case | 104.42 | 62.25 | 407.06 | 0.12572 | 38.39 | 9.43% | 1.11 | 11.8 | 64 | - | 11.8
Summer Peak | LORETTO - PONTIAC 345 kV ckt 1 | 345 | 11.47 | 222 | CE | Base Case | 102.11 | 59.9 | 407.06 | 0.12572 | 38.39 | 9.43% | 0.64 | 6.7673 | 36.704 | - | 6.7673