## AG1-298
Summer Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
STILLWELL - DUMONT Ckt #1 345 kV | 345 | 1409 | Breaker | COMED_P4_112-65-BT3-4__ | 218.07 | 225.62 | 36.64 | 0.1886 | 94.2987 | 77.65 | 28.45
BURNHAM _B - SHEFFIELD Ckt #1 345 kV | 345 | 1441 | Breaker | COMED_P4_112-65-BT3-4__ | 112.53 | 120.41 | 3.32 | 0.28467 | 142.3375 | 91.05 | 3.02
Light Load Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
WILTON_4M - WILTON Xfmr #1 345/765 kV | 345/765 | 1379 | Breaker | COMED_P4_112-65-BT2-3__ | 138.42 | 141.16 | 18 | 0.15402 | 77.0091 | 100 | 18
WILTON_3M - WILTON Xfmr #1 345/765 kV | 345/765 | 1379 | Breaker | COMED_P4_112-65-BT5-6__ | 135.81 | 138.52 | 18 | 0.15083 | 75.4167 | 100 | 18
STILLWELL - DUMONT Ckt #1 345 kV | 345 | 1409 | Single | COMED_P1-2_765-L11215__-S | 136.26 | 134.29 | 6.8 | 0.1838 | 91.9023 | n/a | 0
GREENACRE_T - OLIVE Ckt #1 345 kV | 345 | 971 | Single | AEP_P1-2_#695_1681 | 113.43 | 111.34 | 27.8 | 0.09087 | 45.4332 | n/a | 0

## AG2-357
Summer Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
WILTON_3M - WILTON Xfmr #1 345/765 kV | 345/765 | 1379 | Breaker | COMED_P4_112-65-BT5-6__ | 190.46 | 196.06 | 18 | 0.28552 | 71.3804 | 76.52 | 13.77

## AG2-545
Summer Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
AURORA_EC_RP - ELECT_JCT_4R Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_154-45-BT2-3__ | 104.16 | 110.62 | 0.84 | 0.25398 | 101.5917 | 100 | 0.84
ESS_W407M_9T - ESS_W407K_9T Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L16704T | 97.48 | 104.88 | 2.06 | 0.27703 | 110.8128 | 100 | 2.06
WAYNE_R - ESS_W407M_9T_1 Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L16704T | 97.35 | 104.72 | 4.83 | 0.27703 | 110.8128 | 100 | 4.83
ZION_EC _RP - ZION_STA_R Ckt #1 345 kV | 345 | 1201 | Single | COMED_P1-2_345-L2221__R-N | 100.04 | 104.08 | 3.53 | 0.0788 | 31.5186 | 66.36 | 2.34
ESS_W407K_9T - AURORA_EC_RP Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L16704T | 96.5 | 103.9 | 0.51 | 0.27703 | 110.8128 | 100 | 0.51
LIBERTYVI_R - P_HTS_117_R Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_016-45-BT6-11_ | 97.62 | 102.35 | 9.07 | 0.17456 | 69.8225 | 100 | 9.07

## AF2-441
Summer Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
STILLWELL - DUMONT Ckt #1 345 kV | 345 | 1409 | Breaker | COMED_P4_112-65-BT3-4__ | 218.07 | 225.62 | 36.64 | 0.19003 | 27.1367 | 22.35 | 8.19
AF2-359TAP - OLIVE Ckt #1 345 kV | 345 | 971 | Breaker | COMED_P4_112-65-BT4-5__ | 205.44 | 205.66 | 23.46 | 0.09009 | 12.8647 | n/a | 0
ALLEN - RPMONE Ckt #1 345 kV | 345 | 897 | Breaker | AEP_P4_#7445_05MARYSV 765_B | 196.19 | 196.26 | 78.14 | 0.07933 | 11.3285 | n/a | 0
WILTON_3M - WILTON Xfmr #1 345/765 kV | 345/765 | 1379 | Breaker | COMED_P4_112-65-BT5-6__ | 190.46 | 196.06 | 18 | 0.1534 | 21.9052 | 23.48 | 4.23
WILTON_4M - WILTON Xfmr #1 345/765 kV | 345/765 | 1379 | Breaker | COMED_P4_112-65-BT2-3__ | 192.33 | 192.68 | 18 | 0.15664 | 22.3677 | n/a | 0
JEFRSO - CLIFTY Ckt #Z1 345 kV | 345 | 1868 | Breaker | AEP_P4_#6189_05HANG R 765_D1 | 188.81 | 188.84 | 2.56 | 0.10383 | 14.8273 | n/a | 0
UNIV_PK_N_RP - AF2-359_TAP Ckt #1 345 kV | 345 | 971 | Breaker | COMED_P4_112-65-BT4-5__ | 179.64 | 179.93 | 210.94 | 0.09009 | 12.8647 | n/a | 0
AG1-410TAP - MADDOX Ckt #1 345 kV | 345 | 1301 | Breaker | AEP_P4_#7445_05MARYSV 765_B | 169.39 | 169.44 | 13.33 | 0.07699 | 10.9936 | n/a | 0
CRETE_EC_BP - STJOHN Ckt #1 345 kV | 345 | 1399 | Single | AEP_P1-2_#695_1681 | 161.46 | 161.61 | 38.37 | 0.08699 | 6.9592 | n/a | 0
RPMONE - AG1-410_TAP Ckt #1 345 kV | 345 | 1301 | Breaker | AEP_P4_#7445_05MARYSV 765_B | 157.47 | 157.53 | 27.49 | 0.07699 | 10.9936 | n/a | 0
MARYSV - MARYSV Xfmr #2 765/345 kV | 765/345 | 1868 | Breaker | AEP_P4_#7222_05MALIS 765_D | 151.74 | 151.78 | 18 | 0.05471 | 7.8126 | n/a | 0
MON12 - LALLENDORF Ckt #1 345 kV | 345 | 1702 | Tower | ATSI-P7-1-TE-138-025T-A | 148.42 | 148.45 | 75.04 | 0.06448 | 9.2071 | n/a | 0
GREENACRET - OLIVE Ckt #1 345 kV | 345 | 971 | Breaker | COMED_P4_112-65-BT3-4__ | 143.06 | 143.49 | 150.78 | 0.094 | 13.4236 | n/a | 0
AF2-137TAP - MARYSV Ckt #1 765 kV | 765 | 4142 | Breaker | AEP_P4_#7334_05JEFRSO 765_A2 | 142.9 | 142.96 | 81.75 | 0.26006 | 37.136 | n/a | 0
DUMONT - SORENS Ckt #1 765 kV | 765 | 4142 | Breaker | AEP_P4_#7334_05JEFRSO 765_A2 | 133.61 | 133.71 | 7.63 | 0.24289 | 34.6844 | n/a | 0
E_FRANKFO_B - CRETE_EC_BP Ckt #1 345 kV | 345 | 1399 | Single | COMED_P1-2_765-L11215__-S | 131.02 | 131.18 | 7.48 | 0.08856 | 7.0848 | n/a | 0
ST_JOHN_T - GREEN_ACRE Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 130.6 | 131.17 | 0.09 | 0.07724 | 6.1788 | n/a | 0
STJOHN - ST_JOHN_T Ckt #1 345 kV | 345 | 1091 | Single | AEP_P1-2_#695_1681 | 130.59 | 131.16 | 4 | 0.07724 | 6.1788 | n/a | 0
WILTON - DUMONT Ckt #1 765 kV | 765 | 4105 | Tower | COMED_P7-1_345-L0103__R-S_+_345-L0104__B-S | 129.85 | 131.13 | 98.92 | 0.23215 | 33.1506 | 37.78 | 37.37
SORENS - AF2-137_TAP Ckt #1 765 kV | 765 | 4142 | Breaker | AEP_P4_#7334_05JEFRSO 765_A2 | 130.93 | 131 | 45.78 | 0.26006 | 37.136 | n/a | 0
MOROCCO - ALLEN Ckt #1 345 kV | 345 | 1793 | Breaker | ATSI-P2-3-TE-345-033T | 130.33 | 130.35 | 4.96 | 0.05686 | 8.1194 | n/a | 0
AD1-103TAP - BEAVER Ckt #1 345 kV | 345 | 1742 | Single | ATSI-P1-2-OEC-345-810 | 129.47 | 129.47 | 18.25 | 0.05568 | 4.4547 | n/a | 0
GREEN_ACRE - GREENACRE_T Ckt #1 345 kV | 345 | 1091 | Breaker | COMED_P4_112-65-BT3-4__ | 127.35 | 127.73 | 0.09 | 0.094 | 13.4236 | n/a | 0
DAV-BE - AD1-103_TAP Ckt #1 345 kV | 345 | 1742 | Single | ATSI-P1-2-OEC-345-810 | 126.83 | 126.83 | 16.85 | 0.05568 | 4.4547 | n/a | 0
MADDOX - E_LIMA Ckt #1 345 kV | 345 | 1868 | Breaker | AEP_P4_#7445_05MARYSV 765_B | 126.56 | 126.59 | 19.02 | 0.07673 | 10.9569 | n/a | 0
DAV-BE - HAYES Ckt #1 345 kV | 345 | 1878 | Single | 238569 02BEAVER 345 907200 AD1-103 TAP 345 1 | 125.37 | 125.38 | 35.11 | 0.05758 | 4.606 | n/a | 0
BURNHAM0R - MUNSTER Ckt #1 345 kV | 345 | 1441 | Breaker | COMED_P4_112-65-BT3-4__ | 123.23 | 123.35 | 5.2 | 0.10189 | 14.5502 | n/a | 0
BURNHAMB - SHEFFIELD Ckt #1 345 kV | 345 | 1441 | Breaker | COMED_P4_112-65-BT3-4__ | 112.53 | 120.41 | 3.32 | 0.09793 | 13.9849 | 8.95 | 0.3
ELDERBERRY - DUMONT Ckt #1 345 kV | 345 | 1868 | Breaker | AEP_P4_#8165_05OLIVE 345_B1 | 120.3 | 120.34 | 8.44 | 0.06483 | 9.2572 | n/a | 0
HAYES - BEAVER Ckt #1 345 kV | 345 | 1844 | Single | 238569 02BEAVER 345 907200 AD1-103 TAP 345 1 | 119.26 | 119.27 | 35.11 | 0.05859 | 4.6875 | n/a | 0
GOODINGS_4B - GOODINGS_3B Ckt #1 345 kV | 345 | 1802 | Single | COMED_P1-2_765-L11215__-S | 118.7 | 118.92 | 0.18 | 0.05041 | 4.0332 | n/a | 0
JEFRSO - JEFRSO Xfmr #2 765/345 kV | 765/345 | 3039 | Breaker | AEP_P4_#6189_05HANG R 765_D1 | 116.98 | 116.99 | 18 | 0.10383 | 14.8273 | n/a | 0
LEMOYN - DAV-BE Ckt #1 345 kV | 345 | 1683 | Single | ATSI-P1-2-TE-345-601 | 115.52 | 115.53 | 12.69 | 0.06789 | 5.4314 | n/a | 0
TANNER - M.FORT Ckt #1 345 kV | 345 | 2151 | Single | AEP_P1-2_#7441_100545-A | 113.56 | 113.57 | 2.5 | 0.06241 | 4.9928 | n/a | 0
AB2-067TAP - KAMMER Ckt #1 765 kV | 765 | 4142 | Single | AEP_P2-1_242516 05MOUNTN 765 242920 05BELMON 765 1 | 112.41 | 112.41 | 43.6 | 0.15686 | 12.5492 | n/a | 0
MARYSV - MALIS Ckt #1 765 kV | 765 | 4142 | Breaker | AEP_P4_#2942_05KAMMER 765_PP | 108.26 | 108.28 | 27.25 | 0.1495 | 21.349 | n/a | 0
COLLINS2M - COLLINS Xfmr #1 345/765 kV | 345/765 | 1379 | Single | COMED_P1-2_765-L2315___-S | 106.83 | 107.13 | 18 | 0.05226 | 4.1806 | n/a | 0
GAVIN - MOUNTN Ckt #1 765 kV | 765 | 4571 | Breaker | AEP_P4_#8075_05MARYSV 765_A2 | 105.99 | 106.01 | 11.99 | 0.13143 | 18.7684 | n/a | 0
OLIVE - COOK Ckt #1 345 kV | 345 | 1409 | Breaker | AEP_P4_#8166_05OLIVE 345_E1 | 105.69 | 105.78 | 14.04 | 0.06994 | 9.9881 | n/a | 0
OLIVE - ELDERBERRY Ckt #1 345 kV | 345 | 1539 | Breaker | AEP_P4_#8165_05OLIVE 345_B1 | 104.11 | 104.17 | 0.33 | 0.06856 | 9.7902 | n/a | 0
BAYSH - DAV-BE Ckt #1 345 kV | 345 | 1878 | Single | ATSI-P1-2-TE-345-602 | 103.31 | 103.32 | 12.21 | 0.06657 | 5.326 | n/a | 0
Light Load Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
STILLWELL - DUMONT Ckt #1 345 kV | 345 | 1409 | Single | COMED_P1-2_765-L11215__-S | 136.26 | 134.29 | 6.8 | 0.18524 | 31.4904 | n/a | 0
GREENACRE_T - OLIVE Ckt #1 345 kV | 345 | 971 | Single | AEP_P1-2_#695_1681 | 113.43 | 111.34 | 27.8 | 0.09115 | 15.4948 | n/a | 0

## AH2-015
Summer Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
J1180_TAP - SULLIVAN Ckt #1 345 kV | 345 | 1466 | Single | EXT_P12:345:DEI-AMIL:AMEREN KANSAS-SUGAR CREEK 34545 | 162.08 | 163.17 | 46.88 | 0.07227 | 7.9499 | 46.77 | 21.93
AF2-041_TAP - ELECT_JCT_B Ckt #1 345 kV | 345 | 1656 | Breaker | COMED_P4_144-45-BT7-8__ | 153.88 | 155.29 | 129.89 | 0.23757 | 26.1329 | 36.88 | 47.9
AG1-434_TAP - AF2-041_TAP Ckt #1 345 kV | 345 | 1656 | Breaker | COMED_P4_144-45-BT6-8__ | 139.14 | 140.54 | 25.92 | 0.23725 | 26.0973 | 100 | 25.92
AF1-012_TAP - AG1-434_TAP Ckt #1 345 kV | 345 | 1656 | Breaker | COMED_P4_144-45-BT6-8__ | 136.5 | 137.9 | 42.56 | 0.23725 | 26.0973 | 100 | 42.56
NELSON_B - AF1-012_TAP Ckt #1 345 kV | 345 | 1656 | Breaker | COMED_P4_144-45-BT6-8__ | 132.58 | 133.98 | 6.55 | 0.23725 | 26.0973 | 100 | 6.549
ELECT_JCT_B - LOMBARD_B Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L16704T | 118.34 | 120.04 | 10.41 | 0.16657 | 18.3228 | 66.47 | 6.92
AF1-280_TAP - LEE_CO_EC_BP Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L11124_ | 112.86 | 116.02 | 2.36 | 0.33049 | 36.3544 | 74.97 | 1.77
NELSON_B - AF1-280_TAP Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L11124_ | 97.78 | 100.99 | 5.3 | 0.33049 | 36.3544 | 74.97 | 3.98

## AH2-204
Summer Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
FREEPORT_RT - ESS_B427_4T Ckt #1 138 kV | 138 | 193 | Tower | COMED_P7-1_138-L11902_B-R_+_138-L17121_R-R-A | 170.54 | 259.28 | 3.15 | 0.9999 | 169.9828 | 100 | 3.15
LANCASTER_R - PECATONIC_B Ckt #1 138 kV | 138 | 275 | Tower | COMED_P7-1_138-L11902_B-R_+_138-L19414GR-R-A | 119.62 | 183.73 | 24.82 | 0.9999 | 169.9828 | 100 | 24.82
PECATONIC_B - WEMPLETOW_R Ckt #1 138 kV | 138 | 275 | Tower | COMED_P7-1_138-L11902_B-R_+_138-L19414GR-R-A | 115.12 | 180.29 | 14.6 | 0.9999 | 169.9828 | 100 | 14.6
LANCASTER_R - FREEPORT_RT Ckt #1 138 kV | 138 | 336 | Tower | COMED_P7-1_138-L11902_B-R_+_138-L17121_R-R-B | 106.37 | 157.18 | 1.43 | 0.99484 | 169.1228 | 100 | 1.428
GARDEN_PR_R - SILVER_LK_R Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L11124_ | 145.54 | 150.57 | 108.85 | 0.18331 | 31.1635 | 38.58 | 42
CHERRY_VA_B - GARDEN_PR_R Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_144-45-BT7-8__ | 133.96 | 140.46 | 56.07 | 0.21403 | 36.3843 | 37.79 | 21.19
ESS_B427_4T - S_PECATON_R Ckt #1 138 kV | 138 | 498 | Tower | COMED_P7-1_138-L11902_B-R_+_138-L17121_R-R-B | 66.08 | 100.46 | 6.05 | 0.9999 | 169.9828 | 100 | 6.05

## AH2-259
Summer Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
PLANO_3M - PLANO Xfmr #1 345/765 kV | 345/765 | 1379 | Breaker | COMED_P4_167-45-BT5-6__ | 134.63 | 138.52 | 18 | 0.28679 | 43.0182 | 82.74 | 14.89
PLANO_4M - PLANO Xfmr #1 345/765 kV | 345/765 | 1379 | Breaker | COMED_P4_167-45-BT9-12_ | 133.93 | 137.48 | 18 | 0.26571 | 39.8564 | 80.65 | 14.52
WILTON - DUMONT Ckt #1 765 kV | 765 | 4105 | Tower | COMED_P7-1_345-L0103__R-S_+_345-L0104__B-S | 129.85 | 131.13 | 98.92 | 0.36398 | 54.5965 | 62.22 | 61.55
PLANO_B - ELECT_JCT_B Ckt #1 345 kV | 345 | 1341 | Breaker | COMED_P4_111-45-L16703_ | 121.98 | 125 | 12.54 | 0.27412 | 41.1179 | 100 | 12.54
BRAIDWOOD_B - AD1-100_TAP Ckt #1 345 kV | 345 | 1528 | Breaker | COMED_P4_086-45-BT1-2__ | 122.89 | 123.98 | 3.26 | 0.10039 | 15.0578 | 100 | 3.26
PLANO_R - ELECT_JCT_3R Ckt #1 345 kV | 345 | 1528 | Breaker | COMED_P4_111-45-L16704T | 117.36 | 120.24 | 12.5 | 0.29588 | 44.3815 | 100 | 12.5

## AH2-290
Summer Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
AE2-341_TAP - W_PLANO_R Ckt #1 138 kV | 138 | 498 | Tower | COMED_P7-1_138-L11106_B-R_+_345-L15502_B-R-A | 130.93 | 139.78 | 5.12 | 0.72134 | 43.2804 | 100 | 5.12
PLANO_3M - PLANO Xfmr #1 345/765 kV | 345/765 | 1379 | Breaker | COMED_P4_167-45-BT5-6__ | 134.63 | 138.52 | 18 | 0.14954 | 8.9726 | 17.26 | 3.11
PLANO_4M - PLANO Xfmr #1 345/765 kV | 345/765 | 1379 | Breaker | COMED_P4_167-45-BT9-12_ | 133.93 | 137.48 | 18 | 0.15936 | 9.5613 | 19.35 | 3.48
W_PLANO _R - PLANO_R Ckt #1 138 kV | 138 | 498 | Tower | COMED_P7-1_138-L11106_B-R_+_345-L15502_B-R-A | 124.03 | 132.87 | 0.33 | 0.72134 | 43.2804 | 100 | 0.33
ELECT_JCT_B - LOMBARD _B Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L16704T | 118.34 | 120.04 | 10.41 | 0.15405 | 9.2432 | 33.53 | 3.49
MONTGOMER_RT - OSWEGO_R Ckt #1 138 kV | 138 | 264 | Breaker | COMED_P4_167-38-TR81___ | 100.81 | 111.72 | 1.15 | 0.50545 | 30.3272 | 100 | 1.15
WATERMAN_B - GLIDDEN_BT Ckt #1 138 kV | 138 | 344 | Breaker | COMED_P4_167-38-L14609_ | 97.85 | 106.02 | 0.57 | 0.48083 | 28.8501 | 100 | 0.57
KEWANEE _23 - AG1-435_TAP Ckt #1 138 kV | 138 | 208 | Breaker | COMED_P4_074-38-L7413__ | 86.28 | 100.03 | 3.52 | 0.67964 | 40.7785 | 58.31 | 2.05

## AH2-339
Summer Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
AB1-122_TAP1 - DRESDEN_R Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_012-45-BT4-5__ | 169.35 | 170.87 | 28.7 | 0.19892 | 21.8808 | 100 | 28.7
AG1-121_TAP - HENNEEPIN_T Ckt #1 138 kV | 138 | 208 | Breaker | COMED_P4_074-38-L15508_ | 154.59 | 168.59 | 26.01 | 0.26989 | 29.6881 | 100 | 26.01
J1180_TAP - SULLIVAN Ckt #1 345 kV | 345 | 1466 | Single | EXT_P12:345:DEI-AMIL:AMEREN KANSAS-SUGAR CREEK 34545 | 162.08 | 163.17 | 46.88 | 0.08224 | 9.0462 | 53.23 | 24.95
AF2-128_TAP - CORBIN Ckt #1 138 kV | 138 | 179 | Single | COMED_P1-2_138-L6101___-S-B | 145.21 | 149.81 | 7.36 | 0.07887 | 8.6762 | 100 | 7.36
TAZEWELL - AB1-122_TAP1 Ckt #1 345 kV | 345 | 1479 | Tower | COMED_P7-1_345-L9806__R-S_+_345-L19601_B-S | 147.09 | 148.78 | 302.27 | 0.22323 | 24.5555 | 100 | 302.27
POWERTON - TOWERLINE Ckt #1 138 kV | 138 | 214 | Breaker | COMED_P4_074-38-L15508_ | 120.61 | 146.64 | 9.52 | 0.45723 | 50.2948 | 100 | 9.52
AG1-005_TAP - AF2-128_TAP Ckt #1 138 kV | 138 | 179 | Single | COMED_P1-2_138-L6101___-S-B | 139.34 | 143.95 | 4.54 | 0.07887 | 8.6762 | 100 | 4.54
KEWANEE _13 - KEWANEE_N Ckt #1 138 kV | 138 | 449 | Tower | COMED_P7-1_138-L6101___-S_+_138-L98105_R-S-B | 121.24 | 128.64 | 0.01 | 0.30517 | 33.5691 | 100 | 0.01
AG1-435_TAP - AG1-121_TAP Ckt #1 138 kV | 138 | 208 | Breaker | COMED_P4_074-38-L15508_ | 112.95 | 126.97 | 2.15 | 0.26989 | 29.6881 | 100 | 2.15
HENNEEPIN_T - HENNEPIN_S Ckt #1 138 kV | 138 | 305 | Breaker | COMED_P4_074-38-L15508_ | 118.78 | 126.18 | 0.24 | 0.2144 | 23.5836 | 100 | 0.24
AF1-280_TAP - LEE_CO_EC_BP Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L11124_ | 112.86 | 116.02 | 2.36 | 0.11033 | 12.1361 | 25.03 | 0.59
TOULON_R - POWERTON Ckt #1 138 kV | 138 | 194 | Bus | COMED_P2-2_111_EJ-345B__1 | 94.41 | 115.03 | 15.91 | 0.29983 | 32.9815 | 100 | 15.91
NELSON_B - AF1-280_TAP Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L11124_ | 97.78 | 100.99 | 5.3 | 0.11033 | 12.1361 | 25.03 | 1.33
KEWANEE_23 - AG1-435_TAP Ckt #1 138 kV | 138 | 208 | Breaker | COMED_P4_074-38-L7413__ | 86.28 | 100.03 | 3.52 | 0.265 | 29.1505 | 41.69 | 1.47

## AH2-341
Summer Results
Monitored Facility | Voltage (kV) | Rating (MVA) | Contingency Type | Contingency | Pre Queue Loading % | Post Queue Loading % | Reinforcement Cost ($MM) | Dfax | Impact (MW) | Cost Allocation (%) | Cost Allocation ($MM)
AF2-041_TAP - ELECT_JCT_B Ckt #1 345 kV | 345 | 1656 | Breaker | COMED_P4_144-45-BT7-8__ | 153.88 | 155.29 | 129.89 | 0.17892 | 44.729 | 63.12 | 81.99
GARDEN_PR_R - SILVER_LK_R Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_111-45-L11124_ | 145.54 | 150.57 | 108.85 | 0.19844 | 49.6093 | 61.42 | 66.85
CHERRY_VA_B - GARDEN_PR_R Ckt #1 345 kV | 345 | 1479 | Breaker | COMED_P4_144-45-BT7-8__ | 133.96 | 140.46 | 56.07 | 0.23956 | 59.8899 | 62.21 | 34.88
AG1-423_TP - WAYNE_B Ckt #1 345 kV | 345 | 2058 | Breaker | COMED_P4_138-45-BT23-45 | 132.31 | 134.89 | 19.86 | 0.22796 | 56.9901 | 100 | 19.86
AG1-119_TAP - AG1-423_TP Ckt #1 345 kV | 345 | 2058 | Breaker | COMED_P4_138-45-BT23-45 | 127.69 | 130.27 | 0.2 | 0.22796 | 56.9901 | 100 | 0.2
AB1-089_POI - AG1-119_TAP Ckt #1 345 kV | 345 | 2058 | Breaker | COMED_P4_138-45-BT23-45 | 120.79 | 123.38 | 9.24 | 0.22796 | 56.9901 | 100 | 9.24
BYRON_B - AB1-089_POI Ckt #1 345 kV | 345 | 2058 | Breaker | COMED_P4_138-45-BT23-45 | 110.01 | 112.7 | 5.91 | 0.22796 | 56.9901 | 100 | 5.91
ZION_EC _RP - ZION_STA_R Ckt #1 345 kV | 345 | 1201 | Single | COMED_P1-2_345-L2221__R-N | 100.04 | 104.08 | 3.53 | 0.06392 | 15.9788 | 33.64 | 1.19