## Summer Peak
Model | Monitored Facility | kV | Line Length (mi.) | Contingency Type | Contingency | Dfax | Impact (MW) | Reconductor Cost ($MM) | Replacement Cost ($MM)
Summer Peak | PLANO 3M xfmr 1 345/765 kV | 345/765 | - | Breaker | COMED_P4_167-45-BT5-6__ | 0.28648 | 582.9872 | - | 18
Summer Peak | PLANO 4M xfmr 1 345/765 kV | 345/765 | - | Breaker | COMED_P4_167-45-BT9-12_ | 0.26628 | 541.8831 | - | 18
Summer Peak | ELECT JCT - LOMBARD ckt 1 345 kV | 345 | 17.64 | Single | COMED_P2-1_111-L11120__ | 0.0841 | 171.1446 | 10.4 | -

## Light Load
Model | Monitored Facility | kV | Line Length (mi.) | Contingency Type | Contingency | Dfax | Impact (MW) | Reconductor Cost ($MM) | Replacement Cost ($MM)
Light Load | AF2-359 TAP - OLIVE ckt 1 345 kV | 345 | 7.33 | Single | AEP_P1-2_#695_1681 | 0.10328 | 210.1823 | 4.3 | -
Light Load | WILTON 4M xfmr 1 345/765 kV | 345/765 | - | Breaker | COMED_P4_112-65-BT2-3__ | 0.15803 | 321.5897 | - | 18
Light Load | ALLEN – RPMONE ckt 1 345 kV | 345 | 24.42 | Breaker | AEP_P4_#7445_05MARYSV 765_B | 0.07287 | 92.9067 | 14.4 | -
Light Load | AD1-100 TAP - WILTON ckt 1 345 kV | 345 | 18.8 | Single | COMED_P1-2_765-L11216__-S | 0.08586 | 174.7329 | 11.1 | -
Light Load | WILTON 3M xfmr 1 345/765 kV | 345/765 | - | Breaker | COMED_P4_112-65-BT5-6__ | 0.15475 | 314.9259 | - | 18
Light Load | ST JOHN - GREEN_ACRE ckt 1 345 kV | 345 | 0.16 | Single | COMED_P1-2_765-L11215__-S | 0.09304 | 189.3394 | 0.1 | -
Light Load | STILLWELL - DUMONT ckt 1 345 kV | 345 | 11.45 | Single | COMED_P1-2_765-L11215__-S | 0.14791 | 301 | 6.8 | -
Light Load | UNIV PK N - AF2-359 TAP ckt 1 345 kV | 345 | 65.92 | Single | AEP_P1-2_#695_1681 | 0.10328 | 210.1823 | 38.9 | -
Light Load | E FRANKFO - CRETE EC ckt 1 345 kV | 345 | 12.68 | Single | COMED_P1-2_765-L11215__-S | 0.1301 | 264.7474 | 7.5 | -
Light Load | ST JOHN - ST JOHN ckt 1 345 kV | 345 | 6.78 | Single | COMED_P1-2_765-L11215__-S | 0.09304 | 189.3394 | 4 | -
Light Load | BURNHAM - MUNSTER ckt 1 345 kV | 345 | 8.82 | Single | COMED_P1-2_765-L11215__-S | 0.12338 | 251.0798 | 5.2 | -
Light Load | GREENACRE - OLIVE ckt 1 345 kV | 345 | 47.12 | Single | AEP_P1-2_#695_1681 | 0.0843 | 171.5429 | 27.8 | -
Light Load | AG1-410 TAP - MADDOX ckt 1 345 kV | 345 | 4.17 | Breaker | AEP_P4_#7445_05MARYSV 765_B | 0.07287 | 85.6196 | 2.5 | -
Light Load | PLANO 4M xfmr 1 345/765 kV | 345/765 | - | Breaker | COMED_P4_167-45-BT8-12_ | 0.30373 | 618.0942 | - | 18
Light Load | J1180 TAP - SULLIVAN ckt 1 345 kV | 345 | 14.65 | Breaker | AEP_P4_#3128_05EUGENE 345_A2 | 0.04681 | 62.2568 | 8.6 | -
Light Load | RPMONE - AG1-410 TAP ckt 1 345 kV | 345 | 8.59 | Breaker | AEP_P4_#7445_05MARYSV 765_B | 0.07287 | 92.9067 | 5.1 | -
Light Load | GREEN_ACRE - GREENACRE ckt 1 345 kV | 345 | 0.16 | Single | AEP_P1-2_#695_1681 | 0.0843 | 171.5429 | 0.1 | -
Light Load | PLANO 3M xfmr 1 345/765 kV | 345/765 | - | Single | COMED_P1-3_TR94_PLANO_R-S | 0.23594 | 480.142 | - | 18
Light Load | BUNSONVILLE - EUGENE ckt 1 345 kV | 345 | 11.51 | Single | AEP_P1-2_#695_1681 | 0.06116 | 124.4633 | 6.8 | -
Light Load | BURNHAM - SHEFFIELD ckt 1 345 kV | 345 | 5.62 | Single | COMED_P1-2_765-L11215__-S | 0.09766 | 198.7339 | 3.3 | -
Light Load | DUMONT - SORENS ckt 1 765 kV | 765 | 91.2 | Breaker | AEP_P4_#7334_05JEFRSO 765_A2 | 0.23949 | 487.3705 | 99.4 | -
Light Load | AF1-090 TAP - 7PANA ckt 1 345 kV | 345 | 6.9 | Single | EXT_P12:345:AMIL::AUSTIN:PANA:1 | 0.03777 | 76.8656 | 4.1 | -
Light Load | ELECT JCT - LOMBARD ckt 1 345 kV | 345 | 17.64 | Breaker | COMED_P4_012-45-BT5-6__ | 0.07391 | 150.4065 | 10.4 | -
Light Load | E FRANKFO - UNIV PK N ckt 1 345 kV | 345 | 5.41 | Single | AEP_P1-2_#695_1681 | 0.10328 | 210.1823 | 3.2 | -

## Grid Resilience
Model | Monitored Facility | kV | Line Length (mi.) | Contingency Type | Contingency | Dfax | Impact (MW) | Reconductor Cost ($MM) | Replacement Cost ($MM)
Light Load | WILTON - DUMONT ckt 1 765 kV | 765 | 90.75 | Tower | COMED_P7-1_345-L6607__B-S_+_345-L97008_R-S-A | 0.37893 | 771.1261 | 98.9 | -